## Sheet1
FILE NAME | DOC TYPE | TC DOC NO | TITLE OF LMI | CUSTODIAN DEPT | ISSUE NO | REVISION | DATE | BMD | SIMHADRI | 04:24:44 | 247903 IDATE:05 | 202223 | MTP | LMI | 202204:24:44 | SUBJECT:REVIEW OF LMI “HIGH PRESSURE PIPE SUPPORT OSYSTEMS” | OPERATION | PRESSURE PARTS | REF.: SMPP | DATE: 05.07.2022 | MM | SUBJECT: REVIEW OF LMI “HIGH PRESSURE PIPE SUPPORT SYSTEMS” | LMI NO: LMI | 002 | THE ABOVE APPROVED LMI WAS PREPARED IN THE MONTH OF FEB.’2021. THE ENVISAGED CHANGES IN LMI ARE | INCORPORATED AS PER DETAILS AT REVISION INDEX OF LMI. | PUT UP FOR APPROVAL PLEASE. | SUBMITTED BY: | राहुल जैन विरष्ठ प्रबंधक | RAHUL JAIN 013328 SENIOR MANAGER | SENIOR MANAGER | RAHULJAIN@NTPC.CO.IN | 9415246668 | 247903 | ON:05 | FEW CHNANGES HAVE BEEN INCORPORATED IN SUBJECT LMI AS PER DETAILS MENTIONED IN SL. NO6 OF REVISION INDEX . | APPROVAL MAY PLEASE BE ACCORDED FOR INCORPORATING THESE CHANGES. | सुरेश बाबु कोल्ला उप महाप्रबंधक | SURESH BABU KOLLA 007980 DY. GENERAL MANAGER | DY. GENERAL MANAGER | SBKOLLA@NTPC.CO.IN | 9490307556 | ON:06 | 17:43:32 | SUBMITNTED FOR APPROVAL | ओम प्रकाश अपर महाप्रबंधक | OM PRAKASH 007105 ADDL. GENERAL MANAGER | ADDL. GENERAL MANAGER | 9650994070 | OMPRAKASH08@NTPC.CO.IN | 16:07:05 | ON:07 | SBMITTEND FOR APPROVAL OF COMPETENT AUTHORITY | िझमिल धर अपर महाप्रबंधक | JHIMLI DHAR 006460 ADDL. GENERAL MANAGER | EEMG | 9650998085 | JHIMLIDHAR@NTPC.CO.IN | ON:11 | 10:02:50 | MAY PLENASE BE ACCORDED APPROVAL. | मैथ्यू ई कोवूर महाप्रबंधक | GENERAL MANAGER | MATHEW EIPE KOVOOR 005637 GENERAL MANAGER | 9650994652 | MEKOVOOR@NTPC.CO.IN | 08:45:40 | ON:17 | कृपया अनुमोदन प्रदान िकया जाए। | MAY BE APPROVED PLEASE. | राजेश कुमार झा महाप्रबंधक | RAJESH KUMAR JHA 003323 GENERAL MANAGER | RKJHA02@NTPC.CO.IN | 9415342046 | 10:30:38 | APPROVNED | िगरीश चन्द्र चौकसे महाप्रबंधक | GIRISH CHANDRA CHOUKSE 002907 GENERAL MANAGER | OF PROJECT | HEAD OF PROJECT | GCCHOUKSE@NTPC.CO.IN | 9425178006 | 12:06:50 | ON:18 | NTPC SIMHADRI | LOCATION MANAGEMENT INSTRUCTION | ISSUE NO.1; REVISION NO. 6.00; DATE: | JULY’2022 | HIGH PRESSURE PIPE | SUPPORT SYSTEMS | APPROVED FOR | IMPLEMENTATION | HOP | LMI APPROVAL DOCUMENTS | 1.0 TITLE OF LMI HIGH PRESSURE PIPE SUPPORT | SYSTEMS | 2.A DOCUMENT CODE LMI | ISSUE NO. | B REVISION | DATE ISSUE1; REV.6.00; JULY 22 | REF.DOCUMENT OD | 3.ORIGINAL | 4.PREPARED BY: SR. MANAGER | 5. CHECKED BY: | AGM BMD SIGNATURE_ | MTC. | GM MTC. SIGNATURE_ | M SIGNATURE_ | GM O | 6. REVIEWED AND APPROVED BY SIGNATURE_ | 7.DATE OF ISSUE | 8.INDEX LIST ENCLOSED. | 10.DISTRIBUTION LIST ENCLOSED. | NTPC LMI SIMHADRI | TITLE: HIGH PRESSURE PIPE SUPPORT SYSTEMS REV: 6.00 | DATE: JULY22 | REF NO. LMI | PAGE : 1 OF 8 | 1.0 INDEX | SECTION TITLE PAGE | 1 INDEX 1 | 2 INTRODUCTION 2 | 3 SCOPE 2 | 4 REFERENCE DOCUMENT 2 | 5 SUPERSEDED DOCUMENT 2 | 6 SPECIFIC INSTRUCTIONS 2 | 7 METOLOGY OF 3 | 8 EXCEPTION REPORTING 4 | 10 RECORD KEEPING 4 | 11 REVIEW 4 | 12 REVISION INDEX 5 | 13 DISTRIBUTION LIST 6 | 14 COMPLIANCE RECORD 7 | 15 PIPELINE SURVEY RECORD 8 | DATE: JULY 22 | PAGE : 2 OF 8 | 2.0 INTRODUCTION | HIGH PRESSURE PIPING CARRYING FLUIDS OF PRESSURES GREATER THAN 30 BAR ARE SUPPORTED BY | CARRYING FLUIDS OF PRESSURES GREATER THAN 30 BAR | CONSTANT LOAD HANGERS | VARIABLE SPRING LOAD | SLIDING SUPPORTS. EVEN THOUGH | RIGID STRUTS | THESE SUPPORT UNITS I.E. CONSTANT | THERMAL | LOADING CAN EXERT SIGNIFICANT ADDITIONAL FORCES ABOVE OR BELOW THE DESIGN LIMITS ON THE | PIPE SYSTEMS WHICH CAN INTURN PRODUCE EXPANSION | CONTRACTION. THEY INTURN INDUCE HIGH | STRESSES WHICH MAY LEAD TO WELD CRACK OR DEFLECTION PROBLEMS AT THE BOILER ERS OR | TURBINE CASINGS. | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH SYSTEM OF PERIODIC PREVENTIVE CHECKING AND | 3.0 SCOPE | THE SCOPE OF THIS LMI IS TO DETAIL THE METS THAT ARE TO BE ADOPTED FOR THE PERIODIC | HRH | HP BYPASS. | FEED WATER | PRESSURE PIPING VIZ. MS | CRH | 4.0 REFERENCE DOCUMENT | CORPORATE CENTER. | 5.0 SUPERSEDED DOCUMENT | HIGH PRESSURE PIPE SUPPORT SYSTEMS REV: 2.00 DATE:APR'2013 | 6.0 SPECIFIC INSTRUCTIONS | FOR SUSTAINED INTEGRITY OF HIGH PRESSURE PIPE SUPPORT SYSTEMS THE FOLLOWING INSTRUCTIONS ARE | TO BE FOLLOWED | A PERIODIC INSPECTION OF HANGER SUPPORTS. | B COMPARISON OF HOT AND COLD SETTING WITH THE DESIGN SETTINGS AND SUITABLE | CORRECTIVE ADJUSTMENT. COLOUR CODING FOR HOT AND COLD READING MARKING ON | HANGER SCALE TO BE DONE. | C INSPECTION OF HANGER SUPPORT OF THE PARTICULAR PIPING IN WHICH THERE IS AN | D RLA AND STRESS ANALYSIS TO BE CARRIED FOR UNITS > 25 YEARS OF AGE. | PAGE : 3 OF 8 | CENTERS | A PREOVERHAUL SURVEY OF HIGH PRESSURE PIPE SUPPORT SYSTEMS TO BE CARRIED OUT AT | UNIT FULL LOAD CONDITION. THIS SURVEY WOULD INCLUDE CHECKING OF INTEGRITY OF | RECORDING OF | SUPPORTS AND SCANTLINGS IN THEIR ‘AS FOUND’ MOVEMENT CONDITION | CLIP DISTORTION | OF PERMANENT AND SAFE APPROACHES FOR CD BAY AND OTHER NONREACHABLE | LOCATIONS TO BE MADE. | TMD | FREQUENCY – ONCE BEFORE EVERY OVERHAUL | EXBHEL EXPERTS. THIS | B SURVEY TO BE CARRIED DURING OVERHAUL ALONG WITH BHEL | WOULD INCLUDE CHECKING OF ALL CONSTANT AND VARIABLE LOAD HANGERS | RESTRAINTS AND | FREQUENCY – DURING EVERY OVERHAUL | C COMPARISON OF SURVEY RESULTS IS TO BE CARRIED OUT WITH DESIGN SETTINGS. ALL THE | DEFECTS ARE TO BE LISTED OUT AND CORRECTIVE ACTION IS TO BE TAKEN TO ATTAIN ORIGINAL | CONDITION INCLUDING REPLACEMENT IF NECESSARY. | CONSTRAINTS OF THE PARTICULAR | PIPING SHALL BE PHYSICALLY INSPECTED AGAINST SNAPPING AND DISTORTIONS. TAKING | LIFTING OF PIPING AND | CORRECTIVE ACTION WOULD INCLUDE REPLACING DAMAGED SUPPORTS | RELOADING OF SUPPORTS | RECORDING OF COLD SET VALUES AND FULL LOAD HOT VALUES AFTER | ANY RECTIFICATION AND COMPARISON WITH DESIGN SETTINGS. | E POSTOVERHAUL SURVEY TO BE CARRIED OUT AT FULL LOAD CONDITION. THIS SURVEY WOULD | INCLUDE CHECKING OF INTEGRITY OF SUPPORTS AND SCANTLINGS IN THEIR ‘AS FOUND’ | MOVEMENT CONDITION | AND CHECKING FOR EVIDENCE OF GROSS CLIP DISTORTION | PIPE WORK FOULING AND ANY | FREQUENCY – AFTER EVERY OVERHAUL | F ALL THE PRE | POSTOVERHAUL AND OVERHAUL SURVEY RESULTS AND EXCEPTIONS ARE TO BE | ENGINEER | SENT TO CORPORATE ENGINEERING AND CORPORATE OS. | 002 PAGE : 4 OF 8 | 8. EXCEPTION REPORTING | THE EXCEPTIONS ENCOUNTERED DURING INSPECTION ARE TO BE REPORTED AS PER THE FOLLOWING | FORMAT: | THE FOLLOWING ARE TO BE TREATED AS SIGNIFICANT EXCEPTIONS | A IF MORE THAN 25% OR THREE ADJACENT VARIABLE SPRING UNITS HAVE BOTTOMED OUT. | B IF THE DEFLECTION OF ANY LIMIT STOP IS IN THE DIRECTION OPPOSITE TO DESIGN | SIMHADRI. | C ANY OTHER CASE IN THE OPINION OF HOP | DESCRIPTION OF UNIT LOCATION OF SUPPORT NO. REMARKS | EXCEPTION NO. EXCEPTION | 9.0 RESPONSIBILITIES | PP FOR BOILER SIDE PIPING | TMD FOR TURBINE SIDE PIPING. | 10.0 RECORD KEEPING | THE RECORDS TO BE MAINTAINED UNDER THIS LMI INCLUDE | A COMPLIANCE RECORD OF THE ACTIVITIES DETAILED UNDER THIS LMI | B REPORTS OF PIPE LINE SURVEY CARRIED OUT | C PROPER RECORD AND HISTORY OF PIPING HANGERS TO BE MAINTAINED AND MAKING HANGER | INTRANET. | REPORT AVAILABLE IN SOFT FORM IN BMD DASHBOARD | D EXCEPTION REPORTING | AREA ENGR. TMD | PR. PARTS | THE ABOVE RECORDS ARE TO BE MAINTAINED BY AREA ENGR. PR. PARTS | 11.0 REVIEW | THIS DOCUMENT SHALL BE REVIEWED BY HOP | SIMHADRI ON TWO YEARLY BASIS. | S NO | NOTE NO :1 | 202619:57:30 | 547276 IDATE:17 | 202526 | 19:57:30 | MAINT. PLNG. | SUBJECT:LMI ON SYSTEM FOR PLANT MODIFICATIONS O | NTPC LIMITED | SIMHADRI SUPER THERMAL POWER STATION | SUB: APPROVAL OF LMI ON "SYSTEM FOR PLANT MODIFICATIONS" | LMI ON "SYSTEM FOR PLANT MODIFICATIONS" IS REVIEWED BASED ON LMI | 006 REV5 | GEN | MARCH 2023 | DEC2020 AND NO CHANGES ARE PROPOSED. | 006 REV. NO.:3 | COSISO00OD | OIN | FORMAT REVISED AS PER LMI | 002 REV: 04 ON GUIDELINES FOR ISSUE OF LMIS AS A CONTROLLED | DOCUMENT | SUBMITTED FOR APPROVAL. | ENCL: | 1. LMI FOR APPROVAL AT ANNEXUREI | MARCH 2023 AT ANNEXUREII | 2. LMI | 3. COSISO00OD | DEC2020 AT ANNEXUREIII | चौ. श्रीवेंकट फणी कुमार उप महाप्रबंधक | SRIVENKATA PHANI KUMAR CH 100247 DY. GENERAL MANAGER | 9440100534 | CHSRIVENKATAPHANIKUMAR@NTPC.CO.IN | 202619:57:30 REF:547276 | NOTE NO:2 O | MAY PL NREVIEW | जे आर वगीर्स अपर महाप्रबंधक | RC:1 | JAYAMOL RACHEL VARUGHESE 006127 ADDL. GENERAL MANAGER | JAYAMOLRV@NTPC.CO.IN | 9440918557 | 11:44:32 | ON:19 | 202611:44:32 REF:547276 | NOTE NO:3 O | LMI RENVIEWED. | MAY KINDLY BE APPROVED. | िदव्य चावला अपर महाप्रबंधक | DIVYA CHAWLA 007348 ADDL. GENERAL MANAGER | DIVYACHAWLA@NTPC.CO.IN | 9425534526 | 12:50:46 | 202612:50:46 REF:547276 | NOTE NO:4 O | SUBMITNTED BY: | RC:2 | 11:20:21 | ON:20 | 202611:20:21 REF:547276 | NOTE NO:5 O | LMI IS NIN LINE WITH THE OD. | FORWARDED FOR FURTHER REVIEW. | नवीन िकशोर अपर महाप्रबंधक | NAVIN KISHORE 006964 ADDL. GENERAL MANAGER | 9650990460 | NAVINKISHORE@NTPC.CO.IN | 202610:04:27 REF:547276 | ON:24 | 10:04:27 | NOTE NO:6 O | हमे ेन्द्र कुमार वमार् महाप्रबंधक | HEMENDRA KUMAR VERMA 006459 GENERAL MANAGER | 7091092468 | HKVERMA02@NTPC.CO.IN | 16:53:57 | 202616:53:57 REF:547276 | NOTE NO:7 O | अहमद कौनैन रज़ा महाप्रबंधक | AHMAD KAUNAIN RAZA 006151 GENERAL MANAGER | AKRAZA@NTPC.CO.IN | 9407064096 | 202619:43:56 REF:547276 | 19:43:56 | NOTE NO:8 O | एस पद्मिप्रय महाप्रबंधक | S PADMAPRIYA 004521 GENERAL MANAGER | TECH SERVICES | 9650992835 | SPADMAPRIYA@NTPC.CO.IN | 09:48:06 | ON:27 | 202609:48:06 REF:547276 | NOTE NO:9 O | LMI IS NIN LINE WITH THE OD. MAY PLEASE BE APPROVED. | 11:51:37 | 202611:51:37 REF:547276 | NOTE NO:10 O | अयासकांता जेना मुख्य महाप्रबंधक | CHIEF GENERAL MANAGER | AYASKANTA JENA 005768 CHIEF GENERAL MANAGER | AJENA@NTPC.CO.IN | 9650991410 | 13:10:51 | 202613:10:51 REF:547276 | NOTE NO:11 O | FLOW DINAGRAM AT PAGE 9 OF THE PROPOSED LMI DOCUMENT ADOPTED FROM COSISO00OD | 006 REV. | M . | NO.:3. DATED DEC 2020 HAS BEEN CORRECTED BY REPLACING GMO | M IN PLACE OF AGMO | FORWARDED FOR KIND APPROVAL PL | RC:3 | 16:14:45 | 202616:14:45 REF:547276 | NOTE NO:12 O | 18:34:45 | 202618:34:45 REF:547276 | NOTE NO:13 O | 202618:49:39 REF:547276 | 18:49:39 | NTPC LTD | 006 | MAR 2023 | ISSUE NO.2 REVISION NO. 5 | SYSTEM FOR PLANT MODIFICATIONS | APPROVED FOR IMPLEMENTATION BY: GGM SIMHADRI | EFFICIENCY MANAGEMENT GROUP | ENERGY | LMI NAME SYSTEM FOR PLANT MODIFICATIONS | LMI NO. LMI | ISSUE NO. 2 REVISION: 5 MAR 2023 | NAME SH DESIGNATION | REVIEWED BY D.P. PATRA GM O | CONTENTS | 1. INTRODUCTION .............................................................................................................. 1 | 2. SCOPE ............................................................................................................................. 1 | 3. SUPERSEDED DOCUMENT .............................................................................................. 1 | 4. RECORDS OF REVISION ................................................................................................... 2 | 5. PROCESS ......................................................................................................................... 2 | 6 REVIEW ........................................................................................................................... 6 | ANNEXURE I ......................................................................................................................... 7 | ANNEXURE – II ..................................................................................................................... 10 | P A G E ¦ 1 | 1. INTRODUCTION | REV. 3. THE LMI SPECIFIES THE DETAIL PROCEDURE OF REGISTRATION AND | TECHNICAL ASSESSMENT OF ALL PROPOSED MODIFICATIONS OF SIMHADRI SUPER THERMAL | POWER STATION AS PER THEIR INTENDED PURPOSE FOR SAFETY OF THE PERSONNEL AND | POWER PLANT EQUIPMENT. THIS LMI IS PREPARED TO LAY DOWN THE SPECIFIC PROCEDURES | 2. SCOPE | OR DESIGN CHANGE | 2.1. THIS LMI SHALL BE APPLICABLE TO ALL MODIFICATIONS OR DESIGN CHANGE TO 4 X 500 MW | EQUIPMENT | COMPONENTS OF SIMHADRI STATION AFTER THE DATE OF ISSUE OF | THIS LMI. FOR MODIFICATIONS MADE PRIOR TO ISSUE OF THIS REVISION | PROCEDURE | DESCRIBED AT CLAUSE NO 5.7 IS TO BE FOLLOWED. | 2.2. THE LMI SHALL NOT BE APPLICABLE TO MODIFICATIONS | DESIGN CHANGE TO BE CARRIED OUT | UNDER CONTRACTUAL OBLIGATIONS OF THE CONTRACTOR UNDER THE CONTRACT IRRESPECTIVE OF | THE PERIOD WHEN SUCH MODIFICATION IS CARRIED OUT. HOWEVER | WHERE | IN SUCH CASES | MODIFICATION IS NECESSARILY TO BE CARRIED OUT BY SIMHADRI BEFORE EXPIRY OF THE | WARRANTY PERIOD OR BEFORE PG TEST | WHICHEVER IS LATER | WRITTEN CONSENT OF THE | CONTRACTOR TO SUCH PROPOSED MODIFICATION SHOULD BE OBTAINED BEFORE CARRYING OUT | AN APPROVAL FROM ENGINEERING SHALL BE TAKEN | THE MODIFICATION. IN ALL SUCH CASES | ROS | COS | WHICH SHALL BE ROUTED THROUGH REGIONAL OS ROS AND CORPORATE OS COS. | COMPONENT | 2.3. THE REFERENCE DESIGN OR DATUM FOR EACH PLANT | SYSTEM | OF THE POWER STATION SHALL BE AS PER THE LAST DOCUMENT APPROVED BY ENGINEERING | OR THE ORIGINAL DESIGN DRAWINGS. | 2.4. THE LMI SHALL NOT BE APPLICABLE TO ‘DEFECTS’ OR ‘REPAIRS’ WHICH REQUIRE EQUIPMENT | TO BE REINSTATED TO THE ORIGINAL CONDITION. | 2.5. FOR THE PURPOSE OF THIS LMI | SYSTEM OR COMPONENT SHALL ALSO INCLUDE LOAD | BEARING STRUCTURES | 3. SUPERSEDED DOCUMENT | 006 REV NO.4 DATE : FEB 2021 | CIVIL MAINT. | 202324 | 431023 IDATE:26 | 17:29:07 | CIVIL MAINT | 202317:29:07 | NTPCSIMH | SUBJECT:137 LMI FOR HANDLING AND DISPOSAL OF GRASS REVISIOON REG | LMI REF. LMI | SYST | 015 WAS PREPARED. THE | AS PER THE OD REF. COSISO00 | CIV | 015 | COPY ATTACHED | NO REVISION IN OD WAS PROPOSED. | SAID OD WAS RECENTLY REVIEWED IN AUGUST 2023 COPY ATTACHED HOWEVER | NO CHANGE | THE LMI NO CHANGE IS BEING PUT UP FOR APPROVAL. | ACCORDINGLY BASED UPON THE RECENT REVIEW | प्रकाश चद्रं गुप्ता विरष्ठ प्रबंधक | PRAKASH CHANDRA GUPTA 101976 SENIOR MANAGER | PRAKASHCGUPTA@NTPC.CO.IN | 9650996413 | ON:26 | 431023 | LMI FONR HANDLING AND DISPOSAL OF GRASS HAS BEEN REVIEWED AND ATTACHED. | THERE IS NO CHANGE IN EXISTING DOCUMENT. | SUBMITTED FOR REVIEW AND APPROVAL PL. | एम सी यादव उप महाप्रबंधक | MADHUP CHANDRA YADAV 057675 DY. GENERAL MANAGER | 9319615566 | MCYADAV01@NTPC.CO.IN | 18:47:26 | ON:28 | DISPOSAL OF GRASS HAS BEEN REVIEWED BY CCOS ON 10.08.2023 AND NO REVISION IN THE | THE ODN FOR HANDLING | SAME IS ENVISAGED. | LMI FOR HANDLING AND DISPOSAL OF GRASS PREPARED AT SIMHADRI HAS BEEN REVIEWED AND NO CHANGE IS PROPOSED | IN THE SAME. | SUBMITTED FOR APPROVAL PLEASE. | महशे अलुगोलु अपर महाप्रबंधक | MAHESH ALUGOLU 006936 ADDL. GENERAL MANAGER | 9650993435 | AMAHESH@NTPC.CO.IN | 10:59:46 | ON:29 | ऊमा शंकर वमार् अपर महाप्रबंधक | UMA SHANKER VERMA 006137 ADDL. GENERAL MANAGER | USVERMA@NTPC.CO.IN | 9650992821 | ON:30 | 09:03:41 | अजय गप्ु ता उप महाप्रबंधक | AJAY GUPTA 008565 DY. GENERAL MANAGER | 9958105993 | AJAYGUPTA04@NTPC.CO.IN | 16:18:18 | धमेर्ंद्र कुमार तोमर अपर महाप्रबंधक | ELECT MAINT | DHARMENDRA KUMAR TOMAR 007286 ADDL. GENERAL MANAGER | DHARMENDRAKUMAR02@NTPC.CO.IN | 9416212079 | ON:31 | 16:29:04 | EMD | तेन्नेिट िवजय कृष्ण अपर महाप्रबंधक | TENNETI VIJAY KRISHNA 007966 ADDL. GENERAL MANAGER | 9437188892 | TVIJAYKRISHNA@NTPC.CO.IN | 10:52:58 | 18:28:23 | सिन्जत मजूमदार अपर महाप्रबंधक | SANJIT MAJUMDAR 005065 ADDL. GENERAL MANAGER | FUEL MANAGEMENT | SMAZUMDAR@NTPC.CO.IN | 9650990065 | 09:57:01 | ON:13 | 15:30:56 | MAY PLENASE APPROVE | धुरजित प्रसाद पात्रा महाप्रबंधक | DHURJATI PRASAD PATRA 004573 GENERAL MANAGER | 8275045446 | DPPATRA@NTPC.CO.IN | 00:19:19 | ON:14 | संजय कुमार िसन्हा महाप्रबंधक | SANJAY KUMAR SINHA 005185 GENERAL MANAGER | SKSINHA06@NTPC.CO.IN | 9431215239 | 10:00:22 | NTPC SIMHADRI. | REV. NO. 2 | ISSUE NO.3 | DATE: AUGUST’2023 | LMI FOR HANDLING AND | DISPOSAL OF GRASS. | GGM | PAGE 1 OF 6 | 1. TITLE OF LMI LMI FOR HANDLING AND DISPOSAL OF GRASS | AUGUST’2023 | DATE ISSUE3; REV.2 | 3. ORIGINAL | REF.DOCUMENT OD: COSISO00 | REV. NO.: 0 DATE: JUNE | 2019 | 4.PRERPARED BY NAME: SHRI. P. C. GUPTA | SR. MGR O | M-CIVIL | MCIVIL | SIGNATURE | 5. CHECKED BY NAME: SHRI. M. C. YADAV | DGM O | NAME: SHRI. MAHESH ALUGOLU | AGM CIVIL | CIVIL | 6. REVIEWED BY NAME: SHRI. MATHEW E KOVOOR | GM MAINT | MAINT | NAME: SHRI. D. P. PATRA | 7. APPROVED BY NAME: SHRI. SANJAY KUMAR SINHA | SIGNATURE: | 8.DATE OF ISSUE | 9.INDEX LIST ENCLOSED. | PAGE 2 OF 6 | HANDLING AND DISPOSAL OF GRASS | INDEX | SL. NO. CONTENTS PAGE NO. | 1. INTRODUCTION 4 | 2. REFERENCE DOCUMENT 4 | 3. SUPERSEDED DOCUMENTS 4 | 4. SCOPE 4 | 5. PROCESS 4 | 6. PROHIBITED ACTIVITIES 5 | 8. REVIEW 6 | 9. APPROVING AUTHORITY 6 | PAGE 3 OF 6 | 1.0 INTRODUCTION | THERE HAVE BEEN INCIDENTS WHEREIN DRY GRASS HAS CAUGHT FIRE AND | BUILDINGS AND OTHER ASSETS. THIS DOCUMENT | DESTROYED EQUIPMENT | GIVES GUIDANCE ON HANDLING AND DISPOSAL OF GRASS AT VARIOUS LOCATIONS | SO AS TO AVOID SUCH INCIDENCES. | 2.0 REFERENCE DOCUMENT | COSISO00 | 3.0 SUPERSEDED DOCUMENTS | NIL | 4.0 SCOPE | BIODEGRADABLE WASTE GENERATED FROM PLANT ARISING OUT OF GRASS | DRY | LEAVES AND SMALL TWIGS. | 5.0 PROCESS: | STORAGE | 5.1 INFRASTRUCTURE | ALL SUCH WASTE SHOULD BE DISPOSED OF USING ENVIRONMENT FRIENDLY | MAKING OF BIOMASS PELLET OR ANY OTHER | OPTIONS LIKE COMPOSTING | SUITABLE MET. THIS WASTE SHOULD BE TRANSPORTED AND STORED AT | STORAGE SHED PROVIDED FOR TEMPORARY STORAGE PRIOR TO DISPOSAL BY | DESIGNATED MET. | PRESCRIBED | 5.2 PROVISIONS IN THE GRASS CUTTING CONTRACT | TRANSPORTATION OF | 5.2.1 THERE SHALL BE PROVISION FOR COLLECTION | THIS WASTE TO THE TEMPORARY STORAGE SHED AS MENTIONED | IT IS NOT POSSIBLE TO TRANSPORT THIS | IN PARA 4.0. IN CASE | PAGE 4 OF 6 | WASTE TO TEMPORARY SHEDS | THE GRASS IS TO BE TRANSPORTED | OUTSIDE THE PLANT PREMISES TO DESIGNATED AREAS. THE | ABOVE ACTIVITY SHOULD BE COMPLETED PREFERABLY ON THE | SAME DAY | BUT NOT LATER THAN THE END OF THE NEXT DAY. | 5.2.2 THE GRASS CUTTING HAS TO BE DONE WHILE THE GRASS IS | GREEN AND IN NO CONDITION THE GRASS CAN BE ALLOWED TO | BECOME DRY. | 5.2.3 THERE SHALL BE PROVISION OF PENALTY IN CASE OF THE | FOLLOWING. |  MIXING OF THIS WASTE WITH CONSTRUCTION WASTE OR | DEMOLITION WASTE OR ANY OTHER TYPE OF WASTE WHEN | TRANSPORTED TO TEMPORARY STORAGE AREA. |  OPEN BURNING BY AGENCY OR ITS REPRESENTATIVE. | 6.0 PROHIBITED ACTIVITIES | FOLLOWING ACTIVITIES ARE STRICTLY PROHIBITED IN HANDLING OF THIS | BIODEGRADABLE WASTE: |  WILD GRASS ALLOWED TO GROW BEYOND 15 CM LENGTH AT ANY | LOCATIONS. |  BURNING OF THIS TYPE OF BIOMASS AT NTPC STATIONS | TOWNSHIP PREMISES. | PROJECTS |  MIXING OF THIS BIOMASS WITH CONSTRUCTION AND DEMOLITION | WASTE MAKING IT UNSUITABLE FOR DISPOSAL USING | ENVIRONMENT FRIENDLY OPTIONS AS MENTIONED IN PARA 4.0. | 7.1 FOLLOWING S ARE RESPONSIBLE FOR GRASS CUTTING OF THE | RESPECTIVE AREAS IDENTIFIED FOR THEM. | AND TRANSFORMER YARDS | PAGE 5 OF 6 | LMI REVIEWED ON 08.06.23 | NO CHANGES WERE | DONE. | DATE: | 189065 | LMI REV | 202122 | 10:18:32 | 202110:18:32 | SYSTEMLMI | 002 REV. NO.: 5 JUNE 2021 | COS-ISO-00-OD | 002 REV. NO.: 5 JUNE 2021 WAS ISSUED IN THE MONTH OF | ANY. RECENTLY A NEW VERSIONCOSISO00OD | 5.4 DELETED | 5.4.1 DRAFT DOCUMENT TO BE SENT TO OTHER CORPORATE FUNCTIONS | 5.4.4 NEW DOCUMENT SHALL START WITH “REV.NO.0” | 5.7 RECORDS AND NUMBERING FOR REVIEW AND | OR REVISION | THE LMI IS REVISED AND NECESSARY CHANGES ARE INCLUDED IN THE LMI. | MAY PLEASE BE APPROVED BY COMPETENT AUTHORITY. | सुबीर देबनाथ विरष्ठ प्रबंधक | SUBIR DEBNATH 101608 SENIOR MANAGER | ON:22 | REVIEWED AND FOUND AS PER THE REVISIONS MADE IN COS DOCUMNET. MAY BE APPROVED. | वाई एम मुरलीकृष्णा अपर महाप्रबंधक | YADLAPALLI MOHANA MURALIKRISHNA 003939 ADDL. GENERAL MANAGER | 11:06:53 | REVIEWED. MAY PL APPROVE. | 16:03:59 | APPROVED | िदवाकर कौिशक मख्ु य महाप्रबंधक | DIWAKAR KAUSHIK 004463 GROUP GENERAL MANAGER | GROUP GENERAL MANAGER | 17:03:25 | LOCATION MANAGEMENT INSTRUCTIONS | REVISION NO: 5 | DATE: JUNE 2021 | HOP SIMHADRI | IMPLEMENTATION BY …………………………………….HOP SIMHADRI | LMI NO LMI | REVISION 5 | DATE: 10 | 2021 | NAME DESIGNATION SIGNATURE | REVIEWED BY G C CHOUKSE GM O | SI. NO. CONTENTS PAGE NO. | PURPOSE | 1 1 | SUPERSEDED DOCUMENTS | 2 1 | RECORDS OF REVISION | 3 1 | DOCUMENT TYPE | 4 1 | PROCESS | 5 2 | REVIEW | 6 6 | CHECKLIST | 7 7 | SMSTPS –NTPC LTD | PAGE 1 | REV. NO.:5 | 1.0 PURPOSE | THIS DIRECTIVE DESCRIBES THE FORMAL DOCUMENTATION SYSTEM TO BE IMPLEMENTED WITHIN THE | INITIATION AND CONTROL SYSTEMS FOR DOCUMENTS ISSUED BY THE | IT ESTABLISHES THE PURPOSE | OF CORP. OS AND STATION S FOR IMPLEMENTATION AT | UNITS. | 2.0 SUPERSEDED DOCUMENTS | 002 REV. NO.: 4 ISSUED IN | NOVEMBER 2018. | 3.0 RECORDS OF REVISION | ACTIVITIES | MAY 2021 | S. EXISTING PROVISION REVISED MAY 2021 PROVISION | WILL BE OF THE CONCERNED OF DOCUMENT FOR APPROVAL THROUGH EOFFICE | COS. 5.1 WILL BE THAT OF INCHARGE OF TC | 5.1 | WITH THE SUPPORT OF CONCERNED | OF COS. 5.1 | 2 THE CONCERNED OF COS SHALL DELETED | OBTAIN FROM I | C TC ACTIVITIES OR | THE STANDARD FORMAT | HIS REPRESENTATIVE | OGNS. | FOR PREPARATION OF DRAFT ODS | 5.4 | 3 THE DRAFT SHALL BE CIRCULATED TO STATION THE DRAFT SHALL BE CIRCULATED TO STATION | REDS | OTHER CONCERNED S S | OTHER CONCERNED S | 5.5.1 CORPORATE FUNCTION. THE DRAFT DOCUMENT | 5.5.1 | SHALL ALSO BE POSTED ON OS WEBSITE | 5.4.1 | AT 5.4.4 | 4 ADDED THE FOLLOWING AT 5.4.4: | NEW DOCUMENT SHALL START WITH “REV.NO. | 0”. | 5 DOCUMENTS WOULD BE UPLOADED IN SAP ….. UPLOADED IN SAP AND OS WEBSITE. | AND OS LAN 5.7 THE ISSUE WILL BE THROUGH SOFTCOPY ONLY. | 5.7 | 5.6 | 6 5.8 ADDED THE FOLLOWING 5.7: | OINS SHALL BE REVIEWED | OGN | ALL OD | IF NO REVISION | EVERY TWO YEARS. ON REVIEW | IS ENVISAGED | A SUITABLE RECORD OF THE SAME | WILL BE KEPT AND THE DOCUMENT UPLOADED ON | OS WEBSITE WILL BE STAMPED. IN THIS CASE | THERE WILL BE NO CHANGE IN REVISION NO. | 7 5.9 5.9 OF THE POWER STATION WILL ALSO | 5.9 | COMPRISING OF | OFFSITE | AND ED BY THE | 5.11 : MERGED 5.9 OF THE POWER STATION WILL ALSO | 8 5.10 | 5.10 | 9 5.12 | THE STANDARD FORMAT WITH A DISTINCT NUMBER | AND TAKE APPROVAL OF THE OF THE | PROJECT. ONCE APPROVED | IT WILL BE ENSURED | DOCUMENT IS UPLOADED IN STATION LAN. | 10 5.14 5.11 | 11 5.15 | 5.12 | 5.16 MERGED 5.12 IT WILL BE ENSURED BY THE OF | CHECKED THROUGH AUDITS AS ENVISAGED IN THE | SYSTEM. | M OF THE STATION SHALL | 12 ADDED 5.13 OF O | 5.13 | ENSURE REVIEW OF LMIS EVERY TWO YEARS | THROUGH RESPECTIVE AREA INCHARGE…. | 13 IT WILL ALSO BE NECESSARY FOR THE OF | SYSTEM EXISTS WITHIN THE POWER STATION TO | ADMINISTER THE RECEIPT OF THE DOCUMENTS | IDENTIFIED IN A | B ABOVE AND THE | SUBSEQUENT IMPLEMENTATION OF LMIS AT THE | LOCATION | 4.0 DOCUMENT TYPE | 4.1 CATEGORIES OF DOCUMENTATION | THE FOLLOWING CATEGORIES WILL BE | USED: | IV LOCATION MANAGEMENT INSTRUCTIONS. | THESE CATEGORIES ARE DEFINED AS FOLLOWS: | ODS | THE IMPLEMENTATION OF WHICH IS MANDATORY FOR | ALL APPLICABLE POWER STATIONS. | PAGE 2 | OGNS | OGNS ARE DOCUMENTS CONVEYING ADVICE AND BROAD GUIDANCE ISSUED UNDER THE AUTHORITY OF | THE IMPLEMENTATION OF WHICH WOULD BE | MANDATORY TO THE EXTENT APPLICABLE TO THE PARTICULAR STATION. | OINS | THIS DOCUMENT IS ISSUED UNDER THE AUTHORITY OF OF CORPORATE OS TO PROVIDE | INFORMATION TO POWER STATIONS RELATING TO TECHNICAL MATTERS. THE INFORMATION CONTAINED IN | THESE DOCUMENTS OINS IS TO ASSIST STATION AUTHORITIES AND TO BE ACTED UPON AT THE | DISCRETION OF STATION . | LMIS | 4.1.4 LOCATION MANAGEMENT INSTRUCTIONS LMIS | THESE DOCUMENTS ARE MANAGEMENT INSTRUCTIONS PREPARED AND ISSUED AT STATION LOCATIONS WHICH | GUIDANCE NOTES OR INFORMATION NOTES | AND AUTHORIZED BY THE | ARE DERIVED FROM DIRECTIVES | THE STATION MAY WISH TO | STATION TO INSTRUCT HIS STAFF ON STATION POLICY. IN ADDITION | INCLUDE WITHIN HIS LMI SYSTEM OTHER MATTERS OF STATION POLICY WHICH HE WISHES TO INTRODUCE | AND WHICH ALLOWS HIM TO EFFECTIVELY DISCHARGE HIS MANAGERIAL RESPONSIBILITIES. LMIS ARE BY | DEFINITION SITESPECIFIC | MANDATORY DOCUMENTS. | 5.0 PROCESS | IN CHARGE TECHNICAL COMPLIANCE ACTIVITIES | OVERALL COORDINATOR FOR ISSUE OF ODS | OIN IN THEIR | SERVICES DIVISION SHALL BE RESPONSIBLE FOR IDENTIFICATION OF SUBJECTS OF OD | THE TC DOCUMENT FOR APPROVAL THROUGH EOFFICE WILL BE THAT OF INCHARGE TC ACTIVITIES | WITH SUPPORT OF CONCERNED OF CORPORATE OS. | OINS MAY ARISE FROM ANY | FINALIZATION AND ISSUE OF ODS | 5.2 THE NEED FOR PREPARATION | SHALL IDENTIFY THE SUBJECT | AREA ON WHICH ANY OF THE ABOVE DOCUMENT IS PROPOSED FOR ISSUE AND | LIST OUT THE VARIOUS INPUTS REQUIRED FOR PREPARATION OF SUCH DOCUMENT. | 5.3 THE FOLLOWING MAY BE THE INPUT DOCUMENTS FOR PREPARATION AND FINALIZATION OF | 436379 | D29 | 202312:14:03 | 12:14:03 | FANS O | HAS | 013 | REVISED LMI AND OGN IS ATTACHED. | PUT UP FOR KIND APPROVAL PLEASE. | िरतेश कुमार विरष्ठ प्रबंधक | RITESH KUMAR 101577 SENIOR MANAGER | 9425219186 | RITESHKUMAR01@NTPC.CO.IN | REVIEWNED AND SUBMITTED FOR APPROVAL | 17:11:40 | PLEASE RNEVIEW. | राजेश चावला अपर महाप्रबंधक | RAJESH CHAWLA 007383 ADDL. GENERAL MANAGER | RAJESHCHAWLA@NTPC.CO.IN | 9425534528 | 09:21:08 | REVIEWNED AMD SUBMITTED FOR APPROVAL | पेड़़़्ड़़़ािसगू नाग सुरेश उप महाप्रबंधक | PEDDASINGU NAGA SURESH 008111 DY. GENERAL MANAGER | PNSURESH@NTPC.CO.IN | 8332970695 | 18:28:14 | PL REVIENW. | पीयूष श्रीवास्तव अपर महाप्रबंधक | PIYUSH SRIVASTAVA 006316 ADDL. GENERAL MANAGER | CHEM | PIYUSHSRIVASTAVA@NTPC.CO.IN | 9650999535 | 10:01:12 | MI AND WDA ARE BEING IN PRACTICE AS PER | LMI HANS BEEN REVIEWED AND FOUND THAT MONITORING OF MOISTURE | THE LMI. | MAY PLEASE FORWARDED FOR FURTHER APPROVAL. | रसायन | लिलता देवी वसंत राव उप प्रबंधक रसायन | LDVRAO@NTPC.CO.IN | 8500291983 | 12:19:12 | REVIEWNED AND SUBMITTED FOR APPROVAL. | 12:56:45 | जी एच राव अपर महाप्रबंधक | I MAINT BOILER | G H RAO 006589 ADDL. GENERAL MANAGER | I MAINT- BOILER | GHNRAO@NTPC.CO.IN | 8331016245 | 09:29:15 | PL REVIENW THE LMI W.R.TO THE OGN | टी.आर. राजगोपालन् महाप्रबंधक | TR RAJAGOPALAN 003994 GENERAL MANAGER | TRRAJAGOPAL@NTPC.CO.IN | 9440918024 | 10:01:24 | FOR REVNIEW PLEASE. | मलय कांित जाना अपर महाप्रबंधक | MALAY KANTI JANA 007824 ADDL. GENERAL MANAGER | 9437963403 | MKJANA@NTPC.CO.IN | ON:08 | 18:21:14 | CHECKEND AND FOUND OK AS PER OGN. | सम्राट बिनक प्रबंधक | SAMRAT BANIK 103494 MANAGER | MANAGER | 9425284908 | SAMRATBANIK@NTPC.CO.IN | ON:09 | 15:19:24 | िवमल वािड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़लाल शाह उप महाप्रबंधक | FQA | VIMAL VADILAL SHAH 087028 DY. GENERAL MANAGER | VVSHAH@NTPC.CO.IN | 9427104260 | 09:44:54 | UT SHALL BE CARRIED OUT WITH ASNT | ISNT LEVELII | MPI | LMI HANS BEEN REVIEWED AND PLS BE ENSURE THE DPT | CERTIFIED PERSONEL AS PER THE REQUIREMENT. | MAY PLS FORWARD FOR FURTHER APPROVAL. | वेंकटा श्रीिनवासा राव नुन्ना उप महाप्रबंधक | VENKATA SRINIVASA RAO NUNNA 009626 DY. GENERAL MANAGER | 9440682531 | RAONVSRINIVASA@NTPC.CO.IN | 18:03:01 | NOTE NO:14 O | REVIEWNED. | अजुर्न प्रदीप नायर अपर महाप्रबंधक | ARJUN PRADEEP NAIR 004419 ADDL. GENERAL MANAGER | 9403964693 | APNAIR@NTPC.CO.IN | 18:18:41 | NOTE NO:15 O | LMI HANS BEEN REVISED AS PER REVISION IN REVISED OGN WHICH IS GIVEN IN CLAUSE NO.3.0 ON PAGE NO. 4 OF THE | AS PER REVISED OGN | REVISED LMI AS GIVEN | ATTACHED IN ANNEXURE FOR APPROVAL. CLAUSE NO. 5.5 AS PER REVISED OGN IS NA AS IT FOR | IF APPLICABLE | FLUID COUPLING IF APPLICABLE". | "SERVICING OF VARIABLE SPEED DRIVE VOITH | SUBMITTED FOR KIND APPROVAL OF C.A. HOP SIMHADRI. | 09:46:11 | NOTE NO:16 O | 23:17:22 | NOTE NO:17 O | ON:15 | 09:22:08 | ISSUE NO.1: REVISION NO. 7.00: DATE: AUG.’2023 | GUIDELINES FOR INSPECTION AND | IMPLEMENTATION BY | EMLMICAP | 202317:58:33 | 17:58:33 | 475001 IDATE:11 | SUBJECT:LMI ON CAPACITY TESTING OF DC BATTERIES O | 004 | ELEC | LMI ON CAPACITY TRSTING OF DC BATTERIES IS MODIFIED AS PER THE LMI | CAPACITY TESTING OF DC NICD BATTERIES. | 004 REV. NO.: 02 JULY 2023 | THE NEW REVISION IS APPROVED BASED ON COSISO00OD | ACCORDINGLY MODIFIED LMI IS PROPOSED WITH THE FOLLOWING CHANGES. | • THE CAPACITY TEST OF BATTERY BANKS SHOULD BE CARRIED OUT EVERY 2 YEARS WITH UNIT OVERHAULING | EARLIER | FREQUENCY OF CAPACITY TESTING WAS ANNUALLY IN REV1 | • ANNEXUREV HELP DOCUMENT FOR UPLOADING BATTERY CAPACITY TEST DATA IN SAP | III MODIFIED AS PER NEW OD | • ANNEXURE I | PUT UP FOR APPROVAL. | बाला बालाजी आकुला उप महाप्रबंधक | BALA BALAJI AKULA 009145 DY. GENERAL MANAGER | 8332959245 | ABALABALAJI@NTPC.CO.IN | 475001 | 18:32:13 | 10:54:13 | LMI REVNIEEWED AND FOUND IN ORDER | 20:01:50 | 09:12:13 | 09:14:59 | LMI REVNIEWED AND FORWARDED FOR FURTHER APPROVAL | 09:50:17 | 12:10:47 | ON:16 | 23:52:49 | 17:36:51 | SIMHADRI SUPER THERMAL POWER PROJECT | ISSUE NO: 1 | REVISION: 2 | DATE: JULY 2023 | CAPACITY TESTING OF DC NICD BATTERIES | OF THE PROJECT SIMHADRI | ISSUE 1 REV 2 JULY 2023 | LMI NAME: CAPACITY TESTING OF DC NICD BATTERIES | NAME | LMI NO. : LMI | ISSUE NO. 1 REVISION : 2 DATE: JULY 2023 | PREPARED BY BALABALAJI AKULA DGMEM | VERIFIED BY T. VIJAY KRISHNA AGMEM | VERIFIED BY | D.K. TOMAR AGM EM I | G. HARI NARAYANA RAO | I I | AGM C | D.P. PATRA GMO | REVIEWED BY | P A G E ¦ 2 | SL.NO. CONTENTS PAGE NOS. | 01 INTRODUCTION 3 | 02 SUPERCEDED DOCUMENTS 3 | 03 SCOPE 3 | REFERENCE DOCUMENT 3 | 05 REVISION DETAILS 3 | 06 PROCEDURE 47 | 07 RESPONSIBILITIES 7 | 08 DOCUMENTS 8 | 09 EXCEPTION REPORTING | DESPENSATION | REVIEW 9 | P A G E ¦ 3 | 1. INTRODUCTION : | THE DC POWER SUPPLY IS OF VITAL IMPORTANCE FOR THE SAFETY | SECURITY OF THE | POWER STATION. AT SIMHADRI NICD BATTERIES ARE USED FOR MAIN PLANT | SWITCHYARD AND MAKE UP WATER PUMP HOUSES. THE AMPERE HOUR CAPACITY OF | THE BATTERIES IS TO BE ASSESSED REGULARLY. IN GENERAL THE AH CAPACITY OF THE | RATE OF DEGRADATION DEPENDS ON AMBIENT | BATTERIES DECREASES WITH SERVICE LIFE | SERVICE TEMPERATURE | ASSESS THE ACTUAL BANK CAPACITY AVAILABLE AT THE TIME OF THE TEST | TO IDENTIFY | THE WEAK CELLS AND TAKE SUITABLE CORRECTIVE ACTION. | 2. SUPERCEDED DOCUMENTS: | 004 ISSUE:1 REV :6 DATED: JAN18 | 3. SCOPE: | THIS LMI COVERS THE NICD BATTERY BANKS OF VARIOUS MAKES | TYPES USED FOR | PROVIDING DC POWER SUPPLIES AT NTPC SIMHADRI AS PER THE ANNEXURE1. | 4. REFERENCE DOCUMENT: | 004 ISSUE1 OCT 1994 | 046 REV:0 SEP 2009 | 036 REV:0 AUG 2007 | 004 REV:1 APR 2019 | 5. REVISION DETAILS: | • THE CAPACITY TEST OF BATTERY BANKS SHOULD BE CARRIED OUT EVERY 2 | YEARS WITH UNIT OVERHAULING | EARLIER FREQUENCY OF CAPACITY | TESTING WAS ANNUALLY IN REV1 | • ANNEXUREV HELP DOCUMENT FOR UPLOADING BATTERY CAPACITY TEST DATA IN | SAP | P A G E ¦ 4 | 6. PROCEDURE: | 6.1 BATTERY CAPACITY CHECK | THE CAPACITY TEST SHALL BE CARRIED OUT BIANNUALLY FOR BATTERY BANKS | MENTIONED IN THE ANNEXURE1. | SURGE CAPACITY TESTING IS TO BE DONE PERIODICALLY ON OPPORTUNITY | ADDITIONALLY | SHORT UNIT SHUT DOWN TO ENSURE BATTERY RELIABILITY MENTIONED IN THE | SHORT UNIT SHUT DOWN | ANNEXURE4. |  AS THE BATTERY IS ALREADY ON FLOAT CHARGE | THE CHARGER CAN BE SWITCHED | OFF AND BATTERY TO BE DISCHARGED AT 0.2C5 TILL 1.0 X N CELL VOLTAGE. RECORD | THE CAPACITY | UP TO 1.72 VOLTS PER CELL | 2C5 A FOR 10 HOURS |  RE CHARGE THE BATTERY AT 0 | WHICHEVER IS EARLIER. | @15 TO 25° C FOR KPH TYPE CELLS |  ALLOW REST OF 4 HOURS BEFORE DISCHARGING. | ALL THE CELL VOLTAGES AND |  CAPACITY TEST WILL BE CARRIED OUT AT C5 RATING | TOTAL BANK VOLTAGE WILL BE RECORDED AS PER THE FORMAT IN ANNEXURE2. |  INDIVIDUAL CELL VOLTAGE READINGS SHOULD BE TAKEN BETWEEN RESPECTIVE POSTS | OF LIKE POLARITY OF ADJACENT CELLS | SO AS TO INCLUDE THE VOLTAGE DROP OF THE | INTER CELL CONNECTORS |  THE CELLS SHALL BE DISCHARGED UNTIL THE TERMINAL VOLTAGE FALLS TO 1.0 | VOLTS | CELL OR1.0 X N=TOTAL VOLTAGE FOR A BATTERY BANK. WHERE N = NO. OF | CELL. |  THE MEASUREMENT SHALL NORMALLY BE TAKEN HOURLY 0.2 C 5 DISCHARGING | 0.2 C 5 DISCHARGING | BUT VOLTAGE SHALL BE CHECKED AT 30 MINUTES’ INTERVAL WHEN THE TOTAL | BATTERY VOLTAGE HAS FALLEN BELOW 1.05 X N. |  DISCHARGING OF THE BATTERY BANK IS TO BE CONTINUED UP TO ACHIEVING OF | DO NOT STOP THE DISCHARGING ON ACHIEVING 100% | END VOLTAGE 1.0 X N | CAPACITY. | P A G E ¦ 5 | DO NOT BYPASS OR REMOVE ANY CELL DURING THE DISCHARGE EVEN IF THE | VOLTAGE OF LAGGING CELLS FALLS BELOW 1.0 VOLTS OR REVERSE POLARITY IS | HOWEVER THESE WEAK CELLS CAN BE IDENTIFIED AND REPLACED | OBSERVED | BY HEALTHY ONES LATER |  IF DURING THE CAPACITY TEST ANY CELL VOLTAGE FALLS BELOW 1.0 V OR CELL | POLARITY REVERSAL TAKES PLACE | AND THE | THE CELL WILL NOT BE DISCONNECTED | TEST WILL BE CONTINUED TILL THE TOTAL BANK VOLTAGE REACHES | V MODIFIED WHERE | MODIFIED | VMODIFIED = NO. OF CELLS WITH CORRECT POLARITYX1.0 SUM OF REVERSE | NO. OF CELLS WITH CORRECT POLARITYX1.0 | VOLTAGES. |  TEMPERATURE MEASUREMENT TO BE DONE AT FUSES | JOINTS DURING THE | DISCHARGE AND BOOST CHARGING OF THE BATTERIES. |  BOOST CHARGE THE BATTERIES SUCH THAT THREE CONSECUTIVE READINGS OF THE | CELL VOLTAGE SHOWS NEARLY SAME VALUE. |  CAPACITY CALCULATION= AMPERES X HOURS X TEMPERATURE CORRECTION. | TEMPERATURE CORRECTION FOR +20°C TO +45°C IS 1.0. | TEMPERATURE CORRECTION FOR +20°C TO +45°C IS 1.0 | % CAPACITY AT 25°C WITH C5 RATE = TA | 5 X 100 X TEMPERATURE | CORRECTION. | WHERE TA = ACTUAL TIME TAKEN IN HOURS TO REACH THE END VOLTAGE OF TOTAL | BANK VN | CAPACITY INTERPRETATION | DISCHARGE BATTERY CONDITION | CAPACITY | >100% GOOD CONDITION | EQUAL TO | 90 99.99% SATISFACTORY CONDITION | 85< 90% PLAN FOR REPLACEMENT | < 85% REPLACE THE BATTERY BANK | CHARGER AND CONNECT TO DCDB. |  NORMALIZE THE BATTERY | PAGE 1 OF 4 | ELECT MAINT OFF SITE | LMI INS | 282590 | 17:02:20 | 202317:02:20 | D07 | SUBJECT:SCHEDULE REVIEW OF LMI | 009INSULABTOR | PROTECTION IN POLLUTED ATMOSPHERE O | 009INSULATOR PROTECTION IN | SUBJECT: SCHEDULE REVIEW OF LMI | POLLUTED ATMOSPHERE. | THUNDERSTORM IS REVIEWED AS PER | 009 ON STATION PREPAREDNESS FOR LIGHTNING | SCHEDULE AND INSULATOR PROTECTION IN POLLUTED ATMOSPHERE. | NO CHANGES ARE ENVISAGED. | REVIEW PROPOSAL OF LMI IS SUBMITTED FOR THE KIND APPROVAL. | APPROVING AUTHORITY FOR ABOVE PROPOSAL IS OF THE PROJECT | जे एस एन वी प्रसाद विरष्ठ प्रबंधक | ELECT MAINT OFF | JULUVA SATYANARAYANA VARA PRASAD 068631 SENIOR MANAGER | SITE | 9428815820 | JSNVPRASAD@NTPC.CO.IN | PAGE 2 OF 4 | NO CAHNNGES ENVISAGE. | PERIODIC REVIEW | 13:30:33 | 16:59:55 | 09:57:15 | ON:10 | PAGE 3 OF 4 | 11:45:26 | ON:12 | 09:38:16 | MAY PLENASE APPROVE. | 11:54:10 | PAGE 4 OF 4 | 20:24:38 | 009 | REVISION: 4 | INSULATOR PROTECTION | POLLUTED ATMOSPHERE | DATE: __________________ | LMI NAME : INSULATOR PROTECTION IN POLLUTED | ATMOSPHERE | ISSUE NO. 1 REVISION : 4 DATE: JULY 2023 | PREPARED BY J.S.N.V PRASAD SR. MANAGEREM | VERIFIED BY T.VIJAY KRISHNA AGMEM | C EM | REVIEWED BY D.K.TOMAR AGM I | REVIEWED BY D.P.PATRA GM O | INSULATOR PROTECTION IN POLLUTED ATMOSPHERE | 01 OBJECTIVE 1 | 02 SCOPE | REFERENCE DOCUMENT 1 | SUPERSEDED DOCUMENTS 1 | SPECIFIC INSTRUCTIONS TO BE FOLLOWED 12 | 06 2 | METOLOGY OF IMPLEMENTATION | 08 EXCEPTION REPORTING AND DISPENSATION OF 3 | DEVIATIONS | 09 RECORD KEEPING | 10 REVIEW | PAGE 1 | JULY 2023 | ISSUE 1 REV 4 | 1.0 OBJECTIVE : | POLLUTED ATMOSPHERE MAINLY CONSISTS OF MOISTURE AND AIRBORNE CONTAMINANTS | LIKE SALT | DEPOSITED ON THE INSULATOR SURFACE. CONTAMINATION LEVELS CAN CONTINUE TO | SALTY WATER | RAIN. FOR SUBSTATION AND TRANSMISSION LINES NEARER TO SEA SHORE | SPRAY CAUSES SALT DEPOSITION ON THE INSULATORS. WATER CONDENSES ON THE | INSULATOR WHEN THE INSULATOR SURFACE COOLS BELOW THE DEW POINT TEMPERATURE. | THIS BEHAVIOR IS MOST LIKELY TO OCCUR LATE AT NIGHT OR EARLY IN MORNING. SALTY | CONTAMINATION ALONG WITH MOISTURE PROVIDES A PATH FOR LEAKAGE CURRENT TO FLOW | THEREBY CAUSING TRACKING | FLASHOVERS OF THE INSULATORS. THIS TRACKING | FLASHOVER CAUSES DAMAGE AND FINALLY LEADS TO THE FAILURE OF THE INSULATOR. | FLASHOVERS OF INSULATORS CAN CAUSE GRID DISTURBANCE | POWER INTERRUPTIONS | DAMAGE TO GENERATING UNITS AND STRESSES THE ELECTRICAL EQUIPMENT’S. | THE OBJECTIVE OF THIS LMI IS TO PROTECT THE INSULATORS IN THE POLLUTED | ATMOSPHERE FROM FLASHOVERS THERE BY TO ASSIST IN MAINTAINING THE | STABILITY OF THE GRID. | 2.0 SCOPE: | THIS LMI DOCUMENT COVERS | POST AND SUPPORT INSULATORS. |  400 KV OVER INSULATORS | ASH WATER AND |  PIN AND DISC INSULATORS IN 33 KV SWEET WATER | SEA WATER LINES AND POST AND SUPPORT INSULATORS IN 33KV | SWEET WATER | OUTDOOR SUBSTATIONS OF SEA WATER | AND ASH WATER | RECIRCULATION PUMP HOUSE. |  25MW FLOATING SOLAR 33KV METERING YARD. | 3.0 REFERENCE DOCUMENT: | 4.0 SUPERSEDED DOCUMENTS: | 009 ISSUE: 1 REV: 2 DATED: APRIL 2010 | 5.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED | A FOR 400 KV SWITCHYARD | A VISUAL INSPECTION | B MANUAL CLEANING AREA ENGINEER | C HOT LINE WASHING | B FOR 33KV LINES | SOLAR METERING YARD AND SUBSTATION | C HOTLINE WASHING | 6.0 METOLOGY OF IMPLEMENTATION: | A VISUAL INSPECTION AND THERMOGRAPHY WILL BE CARRIED OUT ONCE IN A MONTH. | B IDENTIFY THE INSULATORS WITH TRACKING | CORONA DISCHARGES DURING THE | CONDITION MONITORING. | C CLEAN MANUALLY THE AFFECTED INSULATORS AS AND WHEN OPPORTUNITY IS | AVAILABLE. | D HOT LINE WASHING ALL 400KV AND 33KV ELEMENTS WILL BE DONE AS TWICE IN A | RESPECTIVE AREA ENGINEERS ARE RESPONSIBLE FOR IMPLEMENTATION AND OVERALL | A MEASUREMENT OF DM WATER CONDUCTIVITY AND SHOULD BE <= 1 ΜS | B DEPLOYED SKILLED MANPOWER SHOULD BE TRAINED FROM NPTI. | C HANDHELD HIGHPRESSURE JETS MUST BE EARTHED BEFORE START OF THE HOT | LINE WASHING. | 8.0 MEASURING EFFECTIVENESS OF HOTLINE WASHING: | EFFECTIVE MEASUREMENT OF HOTLINE WASHING IS DONE BY MEASUREMENT OF | TURBIDITY BEFORE AND AFTER THE HOTLINE WASHING OF AN EQUIPMENT WHEREVER | POSSIBLE. | PAGE 3 | 9.0 EXCEPTION REPORTING AND DISPENSATION OF DEVIATIONS | ANY EXCEPTIONS | DEVIATIONS SHALL BE REPORTED TO EM. | 10.0 RECORD KEEPING: | SWITCHYARD AREA AND 33KV LINES IN HOTLINE WASHING REGISTER. | 11.0 REVIEW: | THIS LMI DOCUMENT WILL BE REVIEWED ONCE IN EVERY TWO YEARS BY OF THE | PROJECT | 437340 | 202316:30:32 | 16:30:32 | 021 | SUBJECT:REVISION OF LMI | TESTING OF STATION EARTHING SYSTEMS O | REVISION OF LMI | 021 HAS BEEN REVISED BY COS IN JULY 2023. NO CHANGES ENVISAGED BY COS. | LMI IS REVIEWED. CHANGES HAVE BEEN MADE IN CLAUSE 2.0 "SCOPE" | CHANGES ARE HIGHLIGTED IN BLUE COLOUR. | PUT UP FOR KIND APPROVAL. | ATTACHMENTS: | AUG 2023 | 1. LMI | REV 7 | JUNE 2021 | REV 1 | 2. OGN | सुिमत कुमार वमार् विरष्ठ प्रबंधक | SUMIT KUMAR VERMA 103292 SENIOR MANAGER | SKVERMA03@NTPC.CO.IN | 8005489736 | REVISEDN LMI IS IN ORDER. | 10:38:50 | 12:51:02 | LMI REVNISED AS DISCUSSED. | 10:20:37 | TO BE RNEVIEWED BY ALL SECTIONS | 21 REVISED JUNE 2021 | LMI FOUND IN ORDER AS PER OGN | 19:27:53 | PLEASE INNCLUDE IN THE SCOPE OF BUILDING EARTHING AS: | 1. CHP CONTROL ROOM | 2. COAL BHAVAN | 3. FUEL BHAVAN | 4. CRUSHER HOUSE#1 | 5. TRACK HOPPER#1 | 6. TRACK HOPPER CONTROL ROOM | मकाला नागश्वे र राव उप महाप्रबंधक | ELECT MAINT MAIN PLANT | ELECT MAINT- MAIN PLANT | MAKALA NAGESWARA RAO 007521 DY. GENERAL MANAGER | MAKALANAGESWAR@NTPC.CO.IN | 8331016103 | 16:07:09 | LMI WINLL BE MODIFIED AFTER ROUTING TO ALL THE SECTIONS. | 16:11:22 | मेड़़़ा नाग राजा उप महाप्रबंधक | MEDA NAGA RAJA 008404 DY. GENERAL MANAGER | MEDANAGARAJA@NTPC.CO.IN | 9437578452 | 17:27:17 | कृष्णा बीसट्टे ी उप महाप्रबंधक | KRISHNA BHEESETTY 009044 DY. GENERAL MANAGER | BKRISHNA@NTPC.CO.IN | 9493546044 | 12:20:17 | सतीश कुमार िसह उप महाप्रबंधक | SATISH KUMAR SINGH 008418 DY. GENERAL MANAGER | SATISHKUMARSINGH@NTPC.CO.IN | 8004940879 | 16:43:28 | सुयार् प्रकाश राव पसुपुरेड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़्ड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ी विरष्ठ प्रबंधक | S ELECT MAINT | SURYA PRAKASH RAO PASUPUREDDY 102528 SENIOR MANAGER | SURYAPRAKASHP@NTPC.CO.IN | 9899678148 | 19:27:50 | REVIEWNED THE LMI W.R.T OGN | 21 REVISED JUNE 2021. | ALL 6 ABOVE LOCATIONS MAY BE INCLUDED IN THE SCOPE OF LMI. | 18:31:20 | THE MENNTIONED AREAS ARE BEING COVERED IN THE LMI. | 11:08:04 | LMI REVNIEWED AND FOUND IN ORDER | 20:04:10 | 09:12:48 | 09:21:04 | 12:16:27 | NOTE NO:18 O | 23:55:40 | NOTE NO:19 O | 17:36:13 | 021 ISSUE: 1 REV: 7 | REVISION: 7 | DATE: AUG 2023 | TESTING OF | STATION EARTHING SYSTEMS | GROUP GENERAL MANAGER SIMHADRI | EARTHING SYSTEMS | ISSUE NO. 1 REVISION : 7 DATE: AUG 2023 | NAME DESIGNATION | PREPARED BY SUMIT KUMAR VERMA SR.MANAGER EM | CHECKED BY A BALA BALAJI DGM EM | CHECKED BY T VIJAY KRISHNA AGM EM | CHECKED BY DHARMENDRA KUMAR TOMAR EM | REVIEWED BY DHURJATI PRASAD PATRA GMO | 858312 | 11:55:47 | 202411:55:47 | 003 | TESTING OF ELECTRIBCAL | PROTECTION SYSTEM O | TESTING OF ELECTRICAL PROTECTION | HAS BEEN REVISED BY COS IN DEC 2023. | RECORDS OF REVISION: | LMI IS REVIEWED AND IS LINE WITH NEW OD. | 16:25:08 | LMI MANY BE UPDATED INLINE WITH REVISED OD. | ALSO RESPONSBILITY TO BE SPECIFIED LIKE FOR CLAUSES 4.4 6 OF OD ETC. | 16:43:57 | LMI IS NUPDATED IN LINE WITH REVISED OD. | SOE SIMULATION IS TO BE JOINTLY CHECKED BY ELECTRICAL | AS PER CLAUSE 4.4 6 OF OD | THE ALARM | SOE OF EQUIPMENTS IS ATTACHED IN LMI AS ANNEXURES. | I GROUP. JOINT PROTOCOL FOR ALARM | UPDATED LMI IS ATTACHED. | ON:02 | 17:57:29 | PUT UP FNOR APPROVAL PLEASE | ON:03 | 09:37:10 | SYSTEM.PDF | 10:36:35 | REVIEWNED AND MAY BE PROCESSED FOR APPROVAL | 20:05:58 | 09:45:00 | 09:08:22 | SOME TYNPOGRAPHICAL ERROR WAS OBSERVED IN THE LMI | SAME IS CORRECTED AND ATTACHED HEREWITH. | 09:20:57 | 09:24:21 | I MAINT | 10:28:44 | AS PERN COSISO00OD | 003 :4.4. :2:FUNCTIONAL TESTING: THE TIME SYNCHRONIZATION OF | NUMERICAL RELAYS AND DCS MAY PLEASE BE ENSURED.IF REQUIRED A PROTOCOL MAY PLEASE BE | SCADA | PREPARED.AS MOST OF THE TIMES DURING ANALYSIS IT IS FOUND THAT SCADA | NUMERICAL RELAY IS NOT TIME SYNCHED. | अजीतकुमार रौशन विरष्ठ प्रबंधक | AJEET KUMAR RAUSHAN 103000 SENIOR MANAGER | AKRAUSHAN@NTPC.CO.IN | 9434077809 | 10:55:41 | 10:59:12 | िवमल वािडलाल शाह उप महाप्रबंधक | 20:13:37 | REVIEWNED AND MAY BE PROCESSED FURTHER. | आिशत रॉय चौधरु ी विरष्ठ प्रबंधक | ASHIT ROY CHOWDHURY 101834 SENIOR MANAGER | AROYCHOWDHURY@NTPC.CO.IN | 9435027019 | 19:18:41 | PL REVIENW THE LMI AND FORWARD FOR FURTHER APPROVAL | 17:29:52 | TESTINGN OF ELECTRICAL ESTABLISHMENT FOR FGD SHOULD ALSO BE COVERED UNDER THIS LMI. | 16:35:07 | AS PER NNOTE NO:18 FGD SYSTEM ALSO MAY BE INCLUDED IN THE SCOPE OF THIS LMI AS AND WHEN THE SYSTEM TRIAL | RUN IS COMPLETED AND HANDED OVER TO NTPC. PRESENTLY LMI IS FORWARDED FOR FURTHER APPROVAL | 18:03:07 | NOTE NO:20 O | 16:30:27 | NOTE NO:21 O | 16:39:46 | NOTE NO:22 O | SYSTEMS ARE HANDED OVER TO NTPC. | 10:17:11 | ON:21 | NOTE NO:23 O | LMI SHNALL BE REVIEWED AGAIN AFTER THE HANDING OVER FGD SYSTEMS TO NTPC. | 16:50:32 | 202317:38:10 | 17:38:10 | 504384 IDATE:21 | SUBJECT:REVIEW OF LMI “WORKING IN CONFINED SPACEO” | SUBJECT: REVIEW OF LMI “WORKING IN CONFINED SPACE” | 047 | THE ABOVE APPROVED LMI WAS PREPARED IN THE MONTH OF AUG.’2021. THE LMI IS DUE FOR REVISION IN THE | MONTH OF SEPT ’2023. NO CHANGES IN LMI ARE INCORPORATED AS PER DETAILS AT REVISION INDEX OF LMI. | राहुल जैन उप महाप्रबंधक | RAHUL JAIN 013328 DY. GENERAL MANAGER | 504384 | सुरेश बाबु कोल्ला अपर महाप्रबंधक | SURESH BABU KOLLA 007980 ADDL. GENERAL MANAGER | 16:29:44 | THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER DETAILS AT REVISION INDEX OF LMI. | ON:23 | 16:40:08 | THE SUBNJECT LMI HAS BEEN REVIEWED AND THE ENVISAGED CHANGES HAVE BEEN INCORPORATED AS PER REFERENCE | DOCUMENT COSISO00OGN | AUG'23. | 047 REV. NO1 | THE CHANGES CARRIED OUT IN THIS REVISED VERSION ARE RELEVANT TO BMD AND TMD AREAS. | 047 REVISION NO1'. | APPROVAL MAY PLEASE BE ACCORDED BY HOP FOR THIS REVISED LMI 'LMIOGN | SUBMITTED FOR REVIEW AND FOR FURTHER APPROVAL PELASE. | 18:58:43 | THE LMNI HAS BEEN REVIEWED AFTER 02 YEARS PERIODICITY. REVISION DONE IN CLAUSE 4.0 MARKED IN BOLD AND | UNDERLINED IN ATTACHED DOC "NEW LMI". | SUBMITTED FOR APPROVAL PLEASE | ON:25 | 11:46:59 | NOTED N | पुली सदािशव रेड़़़्ड़़़ी उप महाप्रबंधक | PULI SADASHIVA REDDY 062135 DY. GENERAL MANAGER | SAFETY | PSADASHIVAREDDY@NTPC.CO.IN | 9425823806 | 18:19:29 | 09:43:18 | 10:48:49 | नीलांजन मंड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ल अपर महाप्रबंधक | ASH HANDLING | NILANJAN MANDAL 007418 ADDL. GENERAL MANAGER | NILANJANMANDAL@NTPC.CO.IN | 9434097418 | 16:01:28 | 17:15:25 | भास्कर वी के कुरीचेट्टी उप महाप्रबंधक | BHASKAR V K KURICHETY 008045 DY. GENERAL MANAGER | KBHASKAR@NTPC.CO.IN | 9445864820 | 18:23:54 | 09:09:43 | MAY PLEASE BE APPROVED. | ASIS KUMAR MUKHOPADHYAY 004586 ADDL. GENERAL MANAGER | AKMUKHOPADHYAY@NTPC.CO.IN | 9434038935 | 16:39:01 | जगनमोहन राव कोनेटी महाप्रबंधक | FGD | KONETI JAGANMOHAN RAO 005969 GENERAL MANAGER | KJRAO@NTPC.CO.IN | 9650998443 | 18:34:56 | देबजीत कुमार कर अपर महाप्रबंधक | DEBJIT KUMAR KAR 003722 ADDL. GENERAL MANAGER | 9650993524 | DEBJITKAR@NTPC.CO.IN | 10:12:41 | REVIEWNED | आन्नप्रगद रमा कोटश्वे रराव अपर महाप्रबंधक | FUEL HAND. OPN | FUEL HAND.- OPN | ANNAPRAGADA RAMA KOTESWARARAO 047211 ADDL. GENERAL MANAGER | 8332988907 | ARKOTESWARARAO@NTPC.CO.IN | 16:16:22 | PLEASE RNEVIEW | शंभू कुमार सुमन अपर महाप्रबंधक | SHAMBHU KUMAR SUMAN 005007 ADDL. GENERAL MANAGER | 9431215296 | SKSUMAN@NTPC.CO.IN | 17:16:38 | 17:35:23 | REVIEWNED. NO CHANGES PROPOSED. | PUT UP FOR FURTHER APPROVAL. | रिश्म रंजन सतपथी विरष्ठ प्रबंधक | RASHMI RANJAN SATAPATHY 100837 SENIOR MANAGER | 9437021584 | RRSATPATHY@NTPC.CO.IN | 09:21:12 | इंद्रजीत जेना विरष्ठ िवशेषज्ञ | INDRAJEET JENA 097748 SR. SPECIALIST | PAEDIATRICIAN | SR. SPECIALIST | INDRAJEETJENA@NTPC.CO.IN | 9437001049 | 11:29:15 | 14:57:00 | 13:40:42 | FOR RESPNONSIBILITY ASSIGNMENT IN LMI | RESPONSBILITY MAY BE ASSIGNED WITH CLARITY. | 10:32:26 | NOTE NO:24 O | 10:53:41 | 967790 | 12:21:07 | D05 | 202412:21:07 | SUBJECT:REVIEW OF LMI “INSPECTION OF BOILER TUBE WELD JOBINTS BY | PHASED ARRAY ULTRASONIC TESTING PAUT” O | PAUT | DATE: 05.03.2024 | SUBJECT: REVIEW OF LMI “INSPECTION OF BOILER TUBE WELD JOINTS BY PHASED ARRAY | ULTRASONIC TESTING PAUT” | THE ABOVE APPROVED LMI WAS PREPARED IN THE MONTH OF FEB.’2019. THE LMI WAS REVISED IN THE MONTH OF | DEC ’2023. CHANGES IN LMI ARE INCORPORATED AS PER DETAILS AT REVISION INDEX OF LMI ARE ARE MARKED IN BOLD . | LMI WINTH REF NO LMI | 047 HAS BEEN REVIEWED AND THE CHANGES INCORPORATED AS PER REF | CA MAY PLEASE ACCORD APPROVAL FOR THIS REVISED VERSION OF THE SUBJECT LMI WITH REF NO | "LMI | 047". | 10:34:30 | FOLLOWINNG REVISIONS DONE IN LMI AS PER REVISED OGN: | 1. PAUT SUTIABILITY ELABORATED AT CLAUSE 7 D. | REVISED ANNEXURE 1 INCORPORATED | 2. FOR MAPPING OF PAUT OF OLD WELD JOINT | SUBMITTED FOR APPROVAL OF LMI NEW LMI DOC ATTACHED AS ANNEXURE. | NEW LMI DOC | 10:44:42 | PL EXAMNINE. | 15:47:50 | AS DISCNUSSED PLS REVIEW. | 12:58:57 | 18:10:55 | NECESSANRY DONE. | SUBMITTED PLEASE | 10:01:59 | SUBMITNTED AFTER MAKING CORRECTIONS AS DISCUSSED. FOR FURTHER REVIEW PLEASE. | 12:17:19 | LMI REVNIEWED. FORWARDED FOR FURTHER APPROVAL PLS. | 15:55:47 | 18:04:38 | 18:10:17 | 18:21:00 | 15:58:04 | सुरेश जॉन ड़ेिवड़ महाप्रबंधक | SURESH JOHN DAVID 005206 GENERAL MANAGER | SJDAVID@NTPC.CO.IN | 9447797541 | 06:43:10 | संजय कुमार िसन्हा मख्ु य महाप्रबंधक | SANJAY KUMAR SINHA 005185 CHIEF GENERAL MANAGER | 20:34:36 | NTPC | ISSUE NO.1; REVISION NO. 2; DATE: DECEMBER 2023 | INSPECTION OF BOILER TUBE WELD | JOINTS BY PHASED ARRAY | ULTRASONIC TESTING PAUT | INSPECTION OF BOILER TUBE | 1.0 TITLE OF LMI WELD JOINTS BY PHASED ARRAY | DATE ISSUE1; REV: 2; DEC’2023 | REF.DOCUMENT COSISO00OGN | REV:0 | 4.PREPARED BY: DGM SIGNATURE | AGM BMD SIGNATURE | GM TS SIGNATURE | M SIGNATURE | 6. REVIEWED AND APPROVED BY SIGNATURE: | TITLE: INSPECTION OF BOILER TUBE WELD JOINTS BY PHASED ARRAY | ULTRASONIC TESTING PAUT REV: 2 DATE: DEC’23 | PAGE : 1 OF 11 | 1.0 INDEX 1 | 2.0 INTRODUCTION 2 | 3.0 SCOPE 2 | 4.0 REFERENCE DOCUMENT 2 | 5.0 SUPERSEDED DOCUMENT 2 | 6.0 SPECIFIC INSTRUCTIONS 3 | 7.0 METOLOGY OF 36 | 9.0 RECORD KEEPING 6 | 10.0 REVIEW 6 | 11.0 REVISION INDEX 7 | 12.0 DISTRIBUTION LIST 8 | 13.0 COMPLIANCE RECORD 9 | 14.0 FORMAT 1011 | APPROVAL | 571710 | D16 | 11:40:45 | 202311:40:45 | FOLLOWING CHANGES ARE DONE IN LMI . | PREVIOUS REV | SECTION BRIEF DETAILS OF CHANGES CURRENT REV | OCT2023 | AMENDMENT RECORD ADDED REV 2 | CAPACITY OF DESALINATION PLANT CORRECTED | OCT2019 REV 2 | INTRODUCTION REV 1 | FROM 240 TPD TO 120 TPD | SUPERSEDED | REV1 DOCUMENTS ADDED REV 1 | SPECIFIC INSTRUCTION LMI ROUTING IS DONE THROUGH ALL | TO BE FOLLOWED CONCERNED S | PUT UP FOR KIND APPROVAL OF CA FOR IMPLEMENTATION OF LMI. | लवन्या कलत्थुरु प्रबंधक | LAVANYA KALATTHURU 103064 MANAGER | 7382621063 | LAVANYAK@NTPC.CO.IN | दीपिशखा वमार् उप महाप्रबंधक रसायन | 9650995244 | DEEPSHIKHAVERMA@NTPC.CO.IN | 10:21:46 | 10:29:00 | 10:44:01 | DUCTS | MAINTENNANCE OF ID FANS | FLUE GAS HEAT EXCHANGERS ETC ARE NOT IN THE PURVIEW OF OFFSITE | MAY PLEASE BE REVIEWED. | 17:47:09 | 18:12:53 | 17:06:46 | सुनीता गुलीिपल्ली प्रबंधक | SUNEETA GULIPILLI 101282 MANAGER | 9493547082 | SUNEETAGULIPILLI@NTPC.CO.IN | 11:29:36 | AS DISCNUSSED PLEASE CORRECT THE PAGE NO. 2 OF 13 AND ALSO ATTACH THE SCHEMATIC DRAWING AS BUILT APPLICABLE | AS BUILT | FOR THE SIMHADRI PLANT AS ANNEXURE TO THIS NEWLY REVISED LMI. | 09:58:31 | AS DISCNUSSED | 10:58:50 | CHANGES DONE AS PROPOSED AT PAGE:2 | PROCESS FLOW DIAGRAM ARE ADDED IN ANNEXURES | SCHEMATIC DRAWING | 12:08:02 | 12:09:56 | PLEASE PNREPARE AND ATTACH A SCHEMATIC OF THE ASBUILT MULTIEFFECT DESALINATION PLANT INSTALLED AT NTPC | SIMHADRI. FOR E.G. THE SCHEME IN THE ATTACHED REVISED LMI DOES NOT SHOW EVEN THE FLUE GAS CIRCULATING FAN | OUTLET MOTORISED DAMPER GATES. KINDLY REDRAW AND ATTACH THE SCHEME TO MATCH THE ACTUAL AS | OR THE INLET | PUMPS | ALL FANS | BUILT CONDITION OF THE MULTIEFFECT DESALINATION PLANT AT SIMHADRI. ALSO INDICATE THEREIN | VALVES AND DAMPERS INDICATING THEIR RESPECTIVE LEGENDS. | 17:31:03 | 17:37:20 | GENERANL LAYOUT OF PLANT IS ATTACHED WITH LMI PL. | 13:11:20 | MAY KINNDLY BE APPROVED | 17:36:57 | GULLOTINNE GATES GG1 AND GG2 SEE DRAWING PLACED IN PAGE NO. 16 OF THE REVISED LMI ALONGWITH THEIR | SEE DRAWING PLACED IN PAGE NO. 16 OF THE REVISED LMI | THE ID FAN EXCLUSIVELY SHOWN IN THE DRAWING ATTACHED ON THE PAGE NO .16 OF THE | RESPECTIVE SLIDING GATES | THE HEAT EXCHANGER AND ALL OTHER COMPONENTS INCLUDING ALL | REVISED LMI AND ALL ITS CONNECTED DAMPERS | PIPING | VALVES AND PUMPS THAT GO INTO WORKING OF THE DESALINATION PLANT SHALL BE MAINTAINED BY OFFSITE | NECESSARY SERVICE CONTRACTS BMC AS WELL AS | MANUAL OF THE DESALINATION PLANT SHALL BE KEPT AVAILABLE AND EXECUTED BY OFFSITE GROUP. ALL ELECTRICAL AND | I RELATED EQUIPMENT PERTAINING TO THE ENTIRE DESLINATION PLANT SHALL BE MAINTAINED BY THE RESPECTIVE | I GROUPS SAME AREA DIVISION TO BE FOLLOWED IN DESALINATION PLANT AS BEING FOLLOWED IN MAIN | I GROUPS. | THE ABOVE IS FOR INFORMATION AND IMPLEMENTATION TO ALL CONCERNED. | UNDERSIGNED MAY PLEASE BE CONTACTED. | FOR ANY FURTHER CLARIFICATIONS AND QUERIES | 13:26:39 | NOTED.N | 19:20:48 | REVIEWN | 20:06:20 | 16:10:57 | HOWEVER CONTROL TYPE ACTUATOR IS TO BE TAKEN | CARE BY C | I AS PER UNIFORM MANITENANCE CIRCULAR EDOS. | 17:00:56 | PL REVIENW THE LMI | 19:28:43 | M CHEM | 988851 | D12 | 12:11:00 | 202412:11:00 | SUBJECT:REVISION OF LMI LMI | 20 ON OPERATING OF B | CONDENSATE POLISHING UNITS O | 20 REV 00 "OPERATING OF CONDENSATE POLISHING UNITS" IS REVIEWED AS PER THE | THIS LMI | 020 REV.NO.:01 JAN2024. THE FOLLOWING CHANGES HAVE BEEN | CORPORATE OGN: OSISO00 OGN | MADE IN THE LMI. | S.NO LMI S.NO REMARKS | 1 4.16 | CONESEP TYPE CPU REGENERATION SYSTEM. | 2 4.17 | PRESERVATION OF | INCORPORATED GUIDELINES FOR SAFE STORAGE | CONESEP FILTER. | 3 4.2L | ANION RINSE CONDUCTIVITY VALUE HAS BEEN REVISED FROM 0.5 | CM TO 0.3 US | 4 4.9 | SPARE RESIN QUANTITY HAS BEEN REVISED | 5 4.12 | ACTIVITIES TABLE | III ADDED | POINTS I | 7 4.6 C | I EQUIPMENT LIST UPDATED | RESIN TESTING PARAMETERS CHANGED. PARAMETERS TOTAL CAPACITY | 8 4.7 | DENSITY | PARTICLE SIZE DISTRIBUTION ADDED | 9 7.0 CHECK LIST FOR RECORDS TO BE MAINTAINED ADDED | SUBMITTED FOR KIND APPROVAL. | नागराजु भास्करानी उप प्रबंधक रसायन | 9446004621 | NAGARAJUBHASKARANI@NTPC.CO.IN | 09:34:39 | 18:30:33 | 15:55:06 | टी वी राजशेखर अपर महाप्रबंधक | T V RAJASEKHAR 007005 ADDL. GENERAL MANAGER | 9650998176 | TVRSEKHAR@NTPC.CO.IN | 09:57:32 | 12:09:51 | 13:10:38 | 18:34:22 | टी वाई रेड्डी उप महाप्रबंधक | I MAINT TURBINE | I MAINT- TURBINE | THEJESWARA REDDY YENNAM 009309 DY. GENERAL MANAGER | THEJAY@NTPC.CO.IN | 9493545586 | 10:16:39 | चन्दन कुमार िनराला विरष्ठ प्रबंधक | CHANDAN KUMAR NIRALA 102031 SENIOR MANAGER | CHANDANKUMARNIRALA@NTPC.CO.IN | 9425178488 | 15:55:57 | 18:53:46 | PL REVIENW AND FORWARD FOR APPROVAL | 10:17:20 | 18:40:26 | हमे ा सुंदर बोद्द ु उप महाप्रबंधक | HEMA SUNDAR BODDU 008465 DY. GENERAL MANAGER | OPN (MAIN PLANT | OPN MAIN PLANT | HSBODDU@NTPC.CO.IN | 8331015740 | 11:02:37 | सुरेश जॉन डेिवड महाप्रबंधक | 16:08:43 | 19:42:22 | REV. NO.: 1 JANUARY 2024 | DATE: 11032024 | ISSUE NO. : 01 | REVISION01 | LMI ON OPERATING OF CONDENSATE POLISHING UNITS | SHRI | NAME SHRI DESIGNATION | PREPARED BY NAGARAJU BHASKARANI DY. MANAGER CHEM | CHECKED BY DEEPSHIKHA VERMA DGM CHEM | CHECKED BY PIYUSH SRIVASTAVA AGMCHEM | CHECKED BY NAVIN KISHORE AGMTMD | CHECKED BY JAYAMOL RACHEL AGMC | CHECKED BY MAHESH ALUGOLU AGMCIVIL | REVIEWED BY SURESH JOHN DAVID GMO | APPROVED BY SANJAY KUMAR SINHA HOP | OPERATING OF CONDENSATE POLISHING UNITS | REVISION:01 | ISSUE:01 | LMI ON OPERATING OF | CONDENSATE POLISHING UNITS | S.NO DESCRIPTION PAGENO | 1.0 INTRODUCTION 3 | 2.0 SUPERSEDED DOCUMENTS 3 | 3.0 SCOPE 3 | 4.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED 318 | 5.0 REFERENCE 18 | 6.0 REVIEW 18 | 7.0 CHECKLIST OF DOCUMENTS TO BE MAINTAINED 19 | ANNEXURE TROUBLESHOOTING FOR CONDENSATE POLISHING UNITS 2021 | ANNEXURE TEMPLATE FOR CPU REGENERATION LOG SHEET 22 | ANNEXURE TEMPLATE FOR CPU PERFORMANCE LOG SHEET 23 | III | ANNEXURE TEMPLATE FOR CPU RESIN MOVEMENT LOG SHEET 24 | ANNEXURE SOP FOR CPU SERVICE DURING UNIT START UP 2526 | ANNEXURE PROTOCOL FOR CPU IN SERVICE PARAMETERS 27 | 12:49:33 | 499476 IDATE:20 | 202312:49:33 | SUBJECT:APPROVAL FOR REVISION OF LMI O | THE LOCATION MANAGEMENT INSTRUCTION LMI OF PERFORMANCE MONITORING OF CW | SYSTEM I.E LMI | PERF | SMSTPS | 008 REVISION IS DONE AS PER REVISION OF TC DOCUMENT. | CONDENSER PERFORMANCE.ACC CONDENSER | IN THIS LMI CHANGES ARE MADE IN MONITORING SHEET OF CW | PERFORMANCE SHEET IS INCLUDED IN THE CHECK LIST. | APPROVING AUTHORITY FOR LMI IS HOP. | पुिष्पता बेहरे ा विरष्ठ प्रबंधक | PUSPITA BEHERA 101583 SENIOR MANAGER | 9425534585 | PUSPITABEHERA@NTPC.CO.IN | 499476 | 09:11:48 | 09:58:15 | 10:00:59 | 17:46:08 | LMI IS NREVIEWED AND FOUND IN LINE WITH OGN. | 09:18:29 | 17:19:12 | 18:25:51 | LMI RENVIEWED W.R.T TO OGN AND LMI OF OTHER STATIONS AND OBSERVATIONS ARE RECORDED AS BELOW. | PAGE NO 7 OF LMI: | POINT C: | II ACID CLEANING TO BE EXPLORED ONLY AFTER CLEANING AND THEREAFTER ASSESSMENT OF TUBES BY EDDY CURRENT | METPRESENTLY IN PRACTICE. RESPONSIBILTY FOR THE SAME MAY SHARED BY TMD | PRESENTLY IN PRACTICE | PASGE NO 8 OF LMI | TMD. | THE ABOVE CHANGES MAY BE INCORPORATED. | PUT UP FOR FURTHER REVIEW. | 19:46:11 | ON:04 | CHANGENS PROPOSED IN NOTE PAGE5 TO BE INCORPORATED. | 09:44:02 | 11:40:20 | REQUIREND CHANGES DONE. PLEASE REVIEW. | 12:24:06 | FORWARNDED | 12:30:38 | 10:03:30 | HT AREAS | MUW | 11:06:15 | 09:40:47 | 17:54:57 | मेड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ा नाग राजा उप महाप्रबंधक | 11:08:59 | 15:53:28 | 10:29:30 | REVIEWNED AND FORWARDED FOR APPROVAL. | 13:21:00 | COPY ATTACHED IN ANNEXURES | PLEASE CNHECK THE SECOND PAGE P NO. 2 OF THE REVISED LMI COPY ATTACHED IN ANNEXURES. IF | P NO. 2 | NO LMI REVIEW | MTNC. | M THEN WHY DO YOU ROUTE IT SO ? | 18:44:29 | 18:47:56 | 11:12:21 | 09:27:20 | 691893 IDATE:30 | 202309:27:20 | SUBJECT:LMI FOR INSPECTION OF CONCRETE CHIMNEYOREG | 005 | THE LMI NO. LMI | REV 3 DATED 25.07.2012 FOR INSPECTION OF CONCRETE CHIMNEY IS | REVIEWED AND NO CHANGES ARE REQUIRED TO BE MADE WITH RESPECT TO PREVIOUS VERSION. | PUT UP FOR APPROVAL OF COMPETENT AUTHORITY. | 691893 | FORWARNDED FOR APPROVAL PLEASE. | 13:04:46 | SUBMITNTED FOR APPROVAL. | 06:36:11 | 17:58:28 | 11:15:33 | 09:32:26 | 005. FORWARDED FOR APPROVAL. | REVIEWNED W.R.T OGN | 10:12:55 | REVIEWNED AND SUBMITTED FOR FURTHER APPROVAL | 16:39:13 | EARTHING | 10:47:43 | 005. FORWARDED FURTHER FOR REVIEW | 16:06:26 | REVIEWEND WRT OGN | 09:36:14 | ON:01 | FORWARNDED FOR APPROVAL | 09:22:42 | 08:29:34 | MAY PLENASE BE APPROVED | 17:57:25 | 09:56:30 | 202118:34:32 | 18:34:32 | 610210 IDATE:06 | 610210 | SUBMITNTED FOR APPROVAL PLEASE. | जयंती गोपी िकरण उप महाप्रबंधक | JAYANTHI GOPI KIRAN 008259 DY. GENERAL MANAGER | GOPIKIRAN@NTPC.CO.IN | 9482234870 | 19:48:25 | MAY PLENASE BE APPROVED. | 13:28:51 | MAY PL NBE APPROVED | जीजीके मूित अपर महाप्रबंधक | GGKMURTHY@NTPC.CO.IN | 9425224918 | 19:48:16 | MAY PLENASE PRIOR TO APPROVAL. | 09:27:54 | THERE ANRE NO CHANGES ENVISAGED IN CCOS DOCUMENT. HENCE THE PROPOSAL MAY BE APPROVED | 9493548377 | YMURALIKRISHNA@NTPC.CO.IN | 15:23:04 | 26762 | BMDMILLS | 202425 | D09 | 12:54:48 | 202412:54:48 | SUBJECT:APPROVAL FOR REVISION OF LMI ON PREVENTION OF COAL PIPE CHOKBING | PROCEDURE FOR REMOVAL OF CHOKE O | PROCEDURE FOR | • LOCAL MANAGEMENT INSTRUCTIONS LMI ON " PREVENTION OF COAL PIPE CHOKING | HAS BEEN REVIEWED AND REVISED VIDE | REMOVAL OF CHOKE " AT NTPC SIMHADRI | “LMI | DATE: APR 2024”. THIS REVISION IS BEING INITIATED | 045 REVISION NO.03 | 045 | TO INCORPORATE THE CHANGES THAT HAS BEEN BROUGHT DUE TO REVISION OF OGN "OGN | MAR. 2024". | 045 REV. NO.02 | REV. NO.1 | OCT 2021" VIDE OGN "OGN | MAR. 2024" WITH | • THE LMI HAS BEEN REVISED AS PER NEW OGN "OGN | FOLLOWING CHANGES: | CLAUSE 8.4 ADDED “GENERAL GUIDELINES FOR PREVENTION OF COAL PIPE CHOKING." AGAINST CLAUSE 5.4 | OF REFERENCE OGN. | CLAUSE 9.5 MODIFIED " TO ENSURE THAT CHOKING OF PF PIPE HAS BEEN CLEARED " AGAINST CLAUSE 6.5 OF | REFERENCE OGN. | CLAUSE 9.6 ADDED "REMOVAL OF TEMPORARY PLATFORMS" AGAINST CLAUSE CLAUSE 6.6 OF REFERENCE | OGN. | • SUBMITTED FOR KIND APPROVAL OF BUH PLEASE. | शिश कांत विरष्ठ प्रबंधक | SHASHI KANT 101559 SENIOR MANAGER | 9425178426 | SHASHIKANT@NTPC.CO.IN | लेख राम स्वणर्कार उप महाप्रबंधक | LEKH RAM SWARNKAR 008125 DY. GENERAL MANAGER | LEKHRAMSWARNKAR@NTPC.CO.IN | 8332959282 | 17:07:30 | THE THRNEE CHANGES INCORPRATED IN LMI AT CLAUSE 8.4 | 9.5 AND 9.6 ARE DETAILED AT PAGE1. | REVIEWED AND SUBMITTED FOR APPROVAL PLEASE. | 10:09:49 | 22:08:50 | PL REVIENW THE LMI AND FORWARD FOR FURTHER SCRUITINY | 09:57:30 | LMI IS NREVIEWED AND FOUND IN LINE WITH OGN. SUBMITTED FOR APPROVAL PLEASE. | 18:44:45 | 15:47:29 | 19:42:39 | REVISION NO. 3.00; DATE: APR’2024 | “PREVENTION OF COAL PIPE | CHOKING AND PROCEDURE FOR | REMOVAL OF CHOKE” | APPROVED FOR IMPLEMENTATION BY HOP | PREVENTION OF COAL PIPE | 1. TITLE OF LMI CHOKING AND PROCEDURE FOR | REMOVAL OF CHOKE | 2. A DOCUMENT CODE LMI | DATE REV: 3.00; APR’2024 | COSISO00OGN | REF.DOCUMENT | REV.NO.02 | MARCH 2024 | 4.PREPARED BY: SR. MANAGER SHASHIKANT | MILLS | DGM MILLS SHRI. L R SWARNKAR | AGM BMD SHRI. OM PRAKASH | GM O SHRI. T.R. RAJAGOPALAN | M SHRI. SURESH JOHN DAVID | 6. REVIEWED AND APPROVED BY SHRI. SANJAY KUMAR SINHA | 7. DATE OF ISSUE | TITLE: PREVENTION OF COAL PIPE CHOKING AND PROCEDURE FOR | REV: 3.00 DATE: APR’24 | 045 PAGE: 1 OF 8 | TITLE | SECTION PAGE | 6.0 SPECIFIC INSTRUCTIONS 2 | CHOKING | 8.0 PREVENTION OF COAL PIPE 3 | 9.0 REMOVAL OF COAL PIPE 4 | 10.0 REVIEW 5 | 11.0 REVISION INDEX 6 | 12.0 DISTRIBUTION LIST 7 | 13.0 COMPLIANCE RECORD 8 | 045 PAGE: 2 OF 8 | 2.0 INTRODUCTION: | COAL PIPE CHOKING IS A SEVERE CHALLENGE FACED IN PULVERIZED COAL POWER PLANT. THE REMOVAL OF | CHOKING IS NOT ONLY A RIGOROUS AND TIME TAKING JOB BUT HAZARDOUS AND PRONE TO FIRE AND EXPLOSION. | THIS DOCUMENT IS PREPARED TO ENSURE AVOIDANCE OF COAL PIPE CHOKING AND SAFE PROCEDURE TO BE | ADOPTED TO REMOVE THE CHOKING IF AT ALL REQUIRED. | 3.0 SCOPE: | THIS LMI ADDRESSES TWO IMPORTANT STEPS TO BE FOLLOWED: | 1. PREVENTION OF COAL PIPE CHOKING BY MONITORING TEMPERATURE OF EACH COAL PIPE PROVIDED IN | CONTROL ROOM. | IN CASE IF THERE IS AN UNAVOIDABLE | 2. PROCEDURE FOR REMOVAL OF COAL FROM CHOKED COAL PIPE | CHOKING. | 045 REV.1 | 045" | DTD. OCT 2021 AND "LMI | REV.2JAN’24. | THE INHERENT MOISTURE IN THE COAL IS PARTIALLY REMOVED BY THE HOT PRIMARY AIR INSIDE THE MILL. | FURTHER | THE PULVERIZED FUEL IS DISCHARGED WITH A MILL OUTLET TEMPERATURE OF 700 – 750 C. IF THIS | MILL OUTLET TEMPERATURE FALLS BELOW 600 C | THERE IS A TENDENCY OF THE PULVERIZED FUEL SETTLING INSIDE | IT IS IMPORTANT TO MONITOR THE MILL OUTLET TEMPERATURE AND COAL PIPE | THE PF PIPES. HENCE | TEMPERATURE ON A CONTINUOUS BASIS. FOR THIS PURPOSE | THERMOCOUPLES HAVE BEEN PROVIDED ON EACH | II UNITS. | AND EVERY COAL PIPES AT CRITICAL LOCATIONS BOTH IN STAGE I | OTHER FACTORS AFFECTING THE SETTLEMENT OF COAL PARTICLES INSIDE THE PF PIPE ARE THE MILL FINENESS AND | THE PF VELOCITY INSIDE THE COAL PIPE. HENCE | IT IS IMPORTANT TO MAINTAIN THESE PARAMETERS WELL | WITHIN THE LIMITS. | SCEOPRN | 045 PAGE: 3 OF 8 | 8.0 PREVENTION OF COAL PIPE CHOKING | 8.1 MONITORING OF COAL PIPE TEMPERATURE: | COAL PIPE TEMPERATURE MEASUREMENT RTD HAVE BEEN PROVIDED IN ALL UNITS | INDICATION IS | AVAILABLE IN CONTROL ROOM. | COAL PIPE TEMPERATURES ARE BEING STRICTLY MONITORED AND MAINTAINED ABOVE 60DEGC DURING THE WHOLE | SHIFT AND IF THERE IS A TEMP DROP BELOW 55 DEGREE C IN ANY COAL PIPE | THEN IT IS DISTINCTIVELY INDICATED IN | THE CONTROL ROOM IN THE LVS BY RED INDICATION. | AT THIS POINT THE COAL FEEDING IN THE ASSOCIATED COAL MILL IS TO BE REDUCED OR FEEDER IS TO BE TAKEN OUT OF | SERVICE TO ENSURE INCREASE IN TEMP. THE TREND OF RISE OF COAL PIPE TEMPERATURE IS OBSERVED IN | COMPARISON TO OTHER COAL PIPES. | AT THE SAME TIME THE COAL PIPE TEMPERATURE IS TO BE MEASURED THROUGH TEMPERATURE GUN AT LOCAL. THIS IS | DONE TO CONFIRM THAT THE FEEDBACK AT CCR IS NOT SPURIOUS. | THE CAP OF SAMPLE POINT IS TO BE OPENED TO ENSURE WHETHER COAL | AIR MIXTURE IS COMING OUT WITH | ALSO | PRESSURE OR NOT. | 8.2 STEPS TO BE FOLLOWED IN CASE COAL PIPE TEMP DOES NOT INCREASE BEYOND 55° C. | IF THERE IS NO SUFFICIENT GAIN | THEN MILL | RISE IN TEMPERATURE OF THE PIPE AS COMPARED TO OTHER 3 COAL PIPES | IS TO BE STOPPED AND AIR IS ISOLATED. | EXCEPT THE AFFECTED ONE | THE REST THREE 3 MDVS EXCEPT THE AFFECTED ONE AND | BURNER ISOLATION GATES ARE TO BE CLOSED. | AFTER THAT COLD AIR IS TO BE CHARGED AFTER KEEPING MILL IN SERVICE UP TO A MAXIMUM OF 40 TON PER HOUR FOR | THAT IS THE | 23 HRS. SAMPLE POINT IS OPENED TO VERIFY WHETHER AIR IS COMING OUT WITH PRESSURE OR NOT | CONFIRMATION THAT CHOKING HAS BEEN CLEARED. | AFTER THIS PROCEDURE MDV AND BURNER ISOLATION GATES OF REST 3 PIPES ARE TO BE OPENED SUBSEQUENTLY AND | HOT AIR IS TO BE CHARGED TO SEE WHETHER THE TEMPERATURE OF THE CONCERNED PIPE RISES. | 8.3 DIRTY PITOT TUBE TEST | TO CHECK ANY COAL PIPE VELOCITY DEVIATION THAT MAY LEAD TO | DIRTY PITOT TUBE TEST TO BE DONE QUARTERLY | 8.4 GENERAL GUIDELINES FOR PREVENTION OF COAL PIPE CHOKING | IMDV | MPO INCLUDING GASKETS TO BE REPLACED IN EACH OH | ACCORDING TO GUARANTEED LIFE. | WHICHEVER IS MORE OR IF PUNCTURED. | IIORIFICE INSPECTION TO BE DONE IN EACH OVERHAULING AND REPLACEMENT TO BE DONE IF DIAMETER. | HAS INCREASED BY MORE THAN 1 %. | SUPPORT IN EACH UNIT OVERHAULING AND RECTIFICATION OF DEFECT IF ANY. | IIIINSPECTION OF HANGER | THEN REASONS | IVIF DEVIATION IN PF VELOCITY IN EACH PIPE COMES MORE THAN 5 % IN DIRTY PITOT TEST | INSPECTION OF | FOR THE SAME TO BE ANALYZED AND CORRECTIVE ACTION INTERNAL INSPECTION OF MILL | VENTURI AREA | INSPECTION OF ORIFICE AND REPLACEMENT IF DEVIATION FOUND SHOULD BE TAKEN AT THE | EARLIEST OPPORTUNITY. AFTER CORRECTION DIRTY PITOT TEST TO BE REPEATED. | V BURNER INLET GATE WHEREVER PROVIDED ARE TO BE KEPT OPERATIVE AND IN HEALTHY CONDITION | WHEREVER PROVIDED | 045 PAGE: 4 OF 8 | 9.0 REMOVAL OF COAL PIPE CHOKING: | AND PERSISTENCE | IF AFTER FOLLOWING THE ABOVE PROCEDURE 8.1 | 8.2 | NO IMPROVEMENT IS OBSERVED | 8.1 | OF THE CHOKE CONTINUES THEN FOLLOWING STEPS FOR “CUTTING WINDOW AND SUBSEQUENT AIR CHARGING” | ARE TO BE FOLLOWED: | 9.1 MILL COOLING IS DONE BY CHARGING COLD AIR AND BRINGING COAL PIPE TEMPERATURE BELOW 40 DEG. | THAT THE | MDV AND BURNER ISOLATION GATE FOR THE CONCERNED PIPE IS TO BE CLOSED. IT IS BETTER | MILL IS FURTHER COOLED TO REACH AMBIENT TEMPERATURE BEFORE START OF WORK. THE PERMIT TO | BE FOLLOWED DURING ISSUANCE OF PERMIT. |  MILL TO BE ISOLATED ELECTRICALLY. |  BURNER ISOLATION GATE FOR CONCERNED PIPE IS TO BE CLOSED. |  SEAL AIR |  INERTING STEAM | THE PERMIT FOR WORKING AT HEIGHT IS TO BE TAKEN PRIOR TO START OF WORK. HOT WORK PERMIT IS | ALSO TO BE TAKEN SIMULTANEOUSLY. | SAFE APPROACH AND PLATFORM FOR REACHING THE HEIGHT IS TO BE BUILT. THE WORKING AREA OF THE PLATFORM | SHOULD BE SUFFICIENTLY LARGE FOR COMFORTABLY CUTTING THE WINDOW AFTER MAINTAINING A SAFE DISTANCE | FROM THE WINDOW. | 9.2 BEFORE CUTTING A WINDOW OF REQUIRED DIMENSION | ENSURE THAT THERE ARE NO ENTRAPPED PRESSURIZED GASES IN THE COAL PIPE. | COAL PIPE I.E. | ON THE PLAN VIEW THROUGH GAS CUTTING. THE WORKER SHOULD KEEP HIS FACE AWAY | FROM THE WINDOW TO AVOID ANY PROBABLE FLAME TO REACH HIS BODY. | THE COLD AIR IS TO BE CHARGED TO BLOW OUT AND REMOVE THE | 9.4 AFTER COMPLETION OF WINDOW CUTTING | THEN THE PROCESS SHOULD BE FINISHED AFTER | CHOKAGES. IF THE REMOVAL OF CHOKE IS ACHIEVED | CLOSING THE WINDOW BY WELDING. BEFORE CHARGING OF COLD AIR ADEQUATE CLEARANCE TO BE LOGGED IN | IF THE REMOVAL OF CHOKE IS NOT ACHIEVED THEN A SECOND WINDOW WOULD BE | 9.5 EVEN AFTER THIS EFFORT | CUT IN THE SAME CROSS SECTION OF PIPE AT ANY OF THE SIDE FACES ACCORDING TO THE SITE CONDITION. | A LOCAL CLEANING OF CHOCKED COAL SHOULD BE DONE | BEFORE STARTING OF CUTTING THE SECOND WINDOW | THROUGH POKING FROM THE ALREADY CUT TOP WINDOW. THE VERY PURPOSE OF SUCH CLEANING IS TO | AVOID ANY CONTACT OF FLAME OF GAS CUTTING SET WITH THE COAL INSIDE THE PIPE DURING CUTTING WORK. | THE PROCESS SHALL CONTINUE TILL THE WHOLE LINE IS CLEARED WHICH CAN BE ENSURED FROM AIR COMING | OUT OF SAMPLE POINT. IF AIR IS COMING OUT FROM SAMPLING POINT | WINDOW THAT WAS CUT FOR | CLEANING TO BE WELDED BACK AND A SMALL NEW WINDOW 100 X 100 TO BE CUT AS NEAR AS POSSIBLE TO | BIG ON MS PORTION AND NOT ON CERAMIC LINED PORTION IN VERTICAL PIPE. COLD AIR IS TO BE | ON MS PORTION AND NOT ON CERAMIC LINED PORTION | CHARGED TO SEE IF AIR IS COMING. IF AIR IS COMING THEN SHUT THE AIR | TAKE THE PTW AND WINDOW TO | BE WELDED BACK. THIS ACTIVITY TO BE CARRIED OUT WITH BIG IN CLOSED CONDITION WHEREVER | PROVIDED. WHILE TAKING MILL IN SERVICE AFTER RETURN OF PTW | TEMPERATURE RISE OF PF PIPE IS TO BE | CHECKED TO ENSURE THAT IT IS EQUAL TO OTHER PF PIPE BEFORE TAKING FEEDER IN SERVICE. | 9.6 TEMPORARY PLATFORMS AND ALL TEMPORARY SUPPORTS TO BE REMOVED AFTER REMOVAL OF CHOKING. | SCEOPR | 202417:38:22 | 17:38:22 | 782573 IDATE:01 | SUBJECT:APPROVAL FOR REVIEW OF LMI O | 001 REVIEW IS DONE AS PER SCHEDULE. IN THIS LMI NO CHANGES HAS BEEN MADE. | APPROVING AUTHORITY OF LMI IS HOP. | 782573 | 17:55:54 | 17:30:51 | 17:53:40 | 09:10:48 | TECHNICAL COMPLIANCE WITHIN | 001 REV: 01 JAN2024 | APPROVED FOR IMPLEMENTATION BY: HOP SMSTPS | 001 REV:01 JAN2024 | REF NO LMI | LMI APPROVAL DOCUMENT | 2 LMI NO. LMI | REFERENCE | 001 | 3 OGN | REV:01 MARCH:1994 | 001 REV: 01 JAN: 2022 | 4 LMI | NAME: PUSPITA BEHERA | 5 PREPARED BY | NAME: AJAY GUPTA | 6 CHECKED BY | NAME: UMA SHANKER VERMA | 7 REVIEWED BY | NAME: SANJAY KUMAR SINHA | 8 APPROVED BY | DESIGNATION: GGM SIMHADRI | 001 REV:01 JAN 2024 | SL.NO. PARTICULARS PAGE NO. | 1.0 INTRODUCTION 4 | 4.0 PURPOSE OF TECHNICAL COMPLIANCE | 6.0 REPORTING PROCEDURES | 7.0 REVIEW | 8.0 APPENDIXA | 3 ¦ P A GE | THE COMPANY’S MANDATORY | EXAMINE COMPLIANCE WITH STATUTORY OBLIGATIONS | THIS LMI ALSO SETS OUT THE SYSTEM OF AUDIT TO BE IMPLEMENTED TO MONITOR AND REPORT | MET OF | ON THE EXTENT OF COMPLIANCE AT NTPC SIMHADRI AND DETAILS OF THE PURPOSE | WORKING AND THE REPORTING PROCEDURE. | REV NO.1 JAN 2022 | COMPLIANCE WITH THE FOLLOWING: | A ALL RELEVANT TECHNICAL STATUTORY REQUIREMENTS THAT APPLY TO THE PLANT AREAS | LISTED IN APPENDIXA OF THIS DOCUMENT. | B ALL DIRECTIVES AND WHERE APPLICABLE | GUIDANCE NOTES | WITHIN THE FORMAL | INVESTIGATION REPORTS. | D ALL OTHER PROCEDURES AND INSTRUCTIONS ISSUED BY OPERATING DIVISION AND OTHER | DIVISION OR CORPORATE FUNCTIONS WHICH HAVE BEEN AUTHORIZED FOR MANDATORY | E ANY OTHER AREAS | TECHNICAL COMPLIANCE AUDITS WILL NOT SEEK TO DUPLICATE AUDITS ALREADY ESTABLISHED | E.G. FINANCE AUDIT. | A TECHNICAL COMPLIANCE AUDIT WILL CONCENTRATE ON COMPLIANCE WITH RELEVANT POLICY BUT | WHERE PROBLEMS ARE IDENTIFIED WITH THE POLICY CONTAINED IN THE COMPANY MANDATORY | DOCUMENTS THESE WILL BE ADDRESSED IN CONJUNCTION WITH THE RESPONSIBLE S. | TECHNICAL COMPLIANCE HAS THE FOLLOWING OBJECTIVES: | A TO MONITOR THE TECHNICAL | STATUTORY AND MANDATORY STANDARDS AS SPECIFIED IN ALL RELEVANT DOCUMENTATION. | 4 ¦ PAGE | WHEN EXAMINING PROCEDURES AND PRACTICES. | B TO NOTIFY MANAGEMENT WHERE THE REQUIRED STANDARDS IDENTIFIED IN A ABOVE | HAVE NOT BEEN ESTABLISHED OR MAINTAINED. | C WHERE STANDARDS ARE NOT BEING ACHIEVED | TO OFFER ADVICE TO LOCATION | MANAGEMENT ON POSSIBLE SOLUTION THAT COULD BE ADOPTED TO SATISFY THE | REQUIREMENTS OF THE RELEVANT DIRECTIVES. | D WHERE APPLICABLE | ENSURE THAT TECHNICAL TRAINING IS IN LINE WITH RELEVANT | DIRECTIVES. | E REPORT THE FINDINGS OF THE AUDIT TO LOCATION MANAGEMENT; THIS WILL INVOLVE A | DRAFT REPORT BEING PRESENTED TO THE STATION MANAGER OR HIS NOMINEE ON | WHICH WILL BE FOLLOWED BY A FORMAL WRITTEN REPORT. | COMPLETION OF THE AUDIT | F INFORM MANAGEMENT OF AREAS OF OPPORTUNITY FOR IMPROVING THE APPLICATION OF | G ASSIST MANAGEMENT IN DEMONSTRATING TO EXTERNAL ORGANIZATIONS THAT THE | COMPANY HAS IN PLACE SOUND MANAGEMENT SYSTEMS FOR THE CONTROL OF TECHNICAL | ISSUES. | 5.1 THE TECHNICAL COMPLIANCE UNIT WILL CARRY OUT AUDITS USING THE RELEVANT | DOCUMENTATION LISTED IN ITS TECHNICAL COMPLIANCE UNIT REGISTER THAT APPLY TO THE | PLANT AREAS IDENTIFIED IN APPENDIXA. | 5.2 THE TECHNICAL COMPLIANCE UNIT WILL CONDUCT DISCRETE INH AUDITS | APPROXIMATELY FIVE DAYS PER AUDIT ON A REGULAR BASIS TO COVER THE PLANT AREAS | APPROXIMATELY FIVE DAYS PER AUDIT | IDENTIFIED IN APPENDIX A TO A NOMINAL 3YEAR CYCLE. THESE AUDITS WILL ASSESS THE | ADEQUACY OF THE MANAGEMENT SYSTEMS DEVELOPED TO IMPLEMENT STATUTORY AND | MANDATORY POLICY CONTAINED IN TECHNICAL DOCUMENTATION. | THE OF TECHNICAL | COMPLIANCE WILL PREPARE AND ISSUE A PROGRAM OF AUDITS. FOLLOWING AGREEMENT | WITH THE OF THE PROJECT ON SUITABLE DATES TO CARRY OUT AN AUDIT AND HIS | REPRESENTATIVE WILL BE CONTACTED AT LEAST TWO WEEKS PRIOR TO THE AUDITS | DISCUSS THE AUDIT OBJECTIVES TO BE INVESTIGATED. | PROVIDE SUITABLE ONSITE FACILITIES AND ACCESS TO ALL RELEVANT DOCUMENTS AND | RECORDS. | 5 ¦ PAGE | THE AUDITORS WILL DISCUSS THE RESULTS OF THE AUDIT | 6.1 AT THE COMPLETION OF AN AUDIT | WITH THE HOP SIMHADRI OR HIS NOMINEE. TE AREAS WHERE NONCOMPLIANCE | HAS BEEN DISCOVERED. | AND APPRAISE OF O | M REGARDING STATUS OF COMPLIANCES. | OR AS AND | THIS DOCUMENT SHALL BE REVIEWED BY OF PROJECT ON A 2YEARLY BASIS | WHEN REQUIRED. | 6 ¦ PAGE | APPENDIXA | PLANT AREAS | PLANT AREAS 1 TURBINE | CONDENSATE | FEED WATER SYSTEM | TURBINE | TECHNICAL COMPLIANCE AUDIT PLANT AREAS | 1.0 TURBINE | 1.1 MAIN TURBINE | BEARINGS | 1.1.1 TG LUBRICATING OIL SYSTEM | CYLINDERS | 1.1.2 TG ROTORS | 1.1.3 STEAM CHESTS | VALVE GEAR | GOVERNORS | 1.1.4 TURBINE SUPERVISORY EQUIPMENT | SUPERVISOR | 1.1.5 HP STEAM PIPEWORK | 1.1.6 FIRE FIGHTING | 2.0 GENERATORS | 2.1 ELECTRICAL GENERATION | 2.2 STATORS AND ROTORS | EXCITERS | 2.3 STATOR COOLING SYSTEM | 2.4 HYDROGEN SYSTEM | 3.0 CONDENSER | 3.1 MAIN CONDENSER | 3.2 CONDENSATE SYSTEM | 4.0 FEED WATER SYSTEM | 4.1 FEED WATER HEATING SYSTEM | 4.2 BOILER FEED PUMP | 5.0 GENERAL | FUEL HANDLING PLANT | PLANT AREAS 2 BOILER PLANT | ASH PLANT | BOILER PLANT | 1.0 BOILER | 1.1 BOILER PLANT | 1.1.1 FLU GAS PASSES | 1.1.2 DRAUGHT PLANT | 1.1.3 PF PLANT | 2.0 FUEL HANDLING PLANT | 2.1 COAL PLANT | 2.2 COAL CONVEYORS AND BUNKERS | 7 ¦ PAGE | LAB | 540318 | 202310:18:31 | 10:18:31 | 020 CLEAN CONDITIOBNS | DURING MAJOR OVERHAULING OF GENERATORS. O | SUBJECT: REVISION OF LMI | 020 CLEAN CONDITIONS DURING MAJOR | OVERHAULING OF GENERATORS. | NO CHANGES ENVISAGED BY COS. ONLY PERIODIC REVIEWING DONE AFTER TWO YEARS. NO CHANGES IN THE DOCUMENT. | MAY PLEASE APPROVE. | रमणीकांत जेना विरष्ठ प्रबंधक | RAMANI KANTA JENA 101544 SENIOR MANAGER | RAMANIKANTAJENA@NTPC.CO.IN | 9438856054 | LMI IS NREVIEWED AND FOUND IN ORDER. | 10:55:44 | 18:15:46 | UPDATEND | 16:40:30 | 09:51:17 | CHECKN LIST ATTACHED. | 10:25:49 | LMI REVNIEWED AND FOUND IN ORDER. | MAY BE APPROVED | 09:15:34 | 17:20:57 | 09:19:08 | 10:11:20 | APPROVNAL MY PLEASE BE ACCORDED FOR THE NEW LMI. | 11:45:27 | 08:50:59 | 11:25:11 | NTPC SIMHADRI 1 | DT OCT 2023 | ISSUE1 | REV2 | 020 | ISSUE NO.: 1 | DATE: OCT 2023 | REVISION; 2 | CLEAN CONDITIONS DURING MAJOR OVERHAULING OF GENERATORS | IMPLEMENTATION BY _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | DATE _ _ _ _ _ _ _ _ _ | NTPC SIMHADRI 2 | LMINAME : CLEAN CONDITIONS DURING MAJOR OVERHAULING OF | GENERATORS | ISSUE NO. 1 REVISION : 2 DATE: OCT 2023 | DESIGNATION SIGNATURE | PREPARED BY SR. MANAGER EM | CHECKED BY DGM EM | CHECKED BY AGM EM | REVIEWED BY AGM EM I | REVIEWED BY GM MAINT | REVIEWED BY GMO | NTPC SIMHADRI 3 | S.NO. DESCRIPTION PAGE NO. | 1.0 OBJECTIVE 4 | 2.0 SCOPE 4 | 3.0 REFERENCE DOCUMENT 4 | 4.0 SUPERCEDED DOCUMENT 4 | 5.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED 4 | 6.0 METOLOGY OF IMPLEMENTATION 47 | 7.0 FREQUENCY OF CHECKING AND MEASUREMENTS 8 | DISPENSATION OF DEVIATIONS 8 | 9.0 EXCEPTION REPORTING | 10.0 RECORD KEEPING 9 | 11.0 REVIEW 9 | 12.0 CHECK LIST 10 | NTPC SIMHADRI 4 | 1.0 OBJECTIVE: | THERE ARE INSTANCES OF SERIOUS DAMAGES CAUSED TO GENERATORS AS A RESULT OF FOREIGN | LMI ALSO PROVIDES GUIDELINES OR MEASURES TO BE TAKEN TO PREVENT INGRESS OF FOREIGN | WORKING | AND REASSEMBLY. | GENERATOR 500MW OF SIMHADRI. | THIS IS APPLICABLE TO UNIT # 1 | 3.0 REFERENCE DOCUMENTS: | 020. | REVISION; 1 | DATE: JAN 2022 | 5.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED: | THE CLEAN CONDITIONS DURING WORK OF GENERATORS SHALL BE CARRIED OUT IN ALL THE UNITS OF | SIMHADRI AS PER 6.0 OF THIS LMI. | WHENEVER GENERATOR END COVERS ARE OPENED AND ANY WORK IS TO BE CARRIED OUT INSIDE | THE FOLLOWING PRECAUTIONS WILL BE TAKEN: | 6.1 PREPARATION: | A BARRIERS: A SECURE PERSONNEL BARRIER SHALL BE ERECTED AROUND THE GENERATOR AT | THE OPERATING FLOOR LEVEL. | B WORKING AREA: THE AREA WITHIN THE BARRIER SHALL BE THOROUGHLY CLEANED | BEFORE ANY PART OF THE GENERATOR IS DISMANTLED. THE CLEAN CONDITIONS SHALL BE | MAINTAINED THROUGHOUT THE WORKING PERIOD. DISMANTLED PMG STATOR | MAIN | EXCITER UNIT AND THREADED OUT GENERATOR ROTOR WOULD BE WRAPPED WITH | 843466 IDATE:23 | 202409:46:12 | 09:46:12 | SUBJECT:REVISION OF APH LMI AS PER CHANGES IN OGN O | 055 | 055" REV. NO.: 1 DEC'2023. | HAS BEEN REVISED AS PER REVISED OGN "COSISO00OGN | कृष्ण लाल विरष्ठ प्रबंधक | KRISHAN LAL 102736 SENIOR MANAGER | KRISHANLAL01@NTPC.CO.IN | 8005442515 | 843466 | REVISIONNS INCORPORATED AS PER REVISED COSISO00OGN | 055 REV. NO.: 1 DECEMBER 2023. | MAY PLZ APPROVE. | 11:15:08 | CHANGENS AS PER REVISED OGN "COSISO00OGN | 055" HAVE BEEN INCORPORATED IN THE REVISED | 055". | VER.1 OF LMI "LMI | HOP MAY KINDLY ACCORD APPROVAL FOR THIS REVISED VERSION OF SUBJECT LMI. | 13:32:37 | 18:08:43 | 09:16:01 | 09:41:08 | 10:32:37 | DURING OVERHAULING OF UNIT1 RECENTLY | PLEASE CNONFIRM WHETHER ALL POINTS AS MENTIONED IN THE LMI | ESPECIALLY CLAUSE NO. 5.5.10. | CONCLUDED HAVE BEEN TAKEN CARE OF | 09:52:59 | 10:24:49 | 09:51:21 | WORK HNAS BEEN COMPLETED AS PER PROTOCOL AND LMI INCLUDING CLAUSE NO 5.5.10. | 17:33:05 | MAY PLZN BE APPROVED. | 16:32:42 | SUBMITNTED FOR APPROVAL PLEASE | 18:35:31 | 20:01:10 | 08:49:13 | REV. NO. : 1 JANUARY 2024 | PRACTICES OF AIR PREHEATERS | TECHNICAL COMPLIANCE SYSTEM | LOCATION MANAGEMENT INSTRUCTION LMI | REV.NO.:1 DATE: JANUARY 2024 | HOP SSTPP | SSTPP | REVISION 1 | JANUARY 2024 | AIR PREHEATERS | 2 DOCUMENT NUMBER LMI | DATE REVISION 1 | 3 ORIGINAL | REF DOCUMENT COSISO00OGN | REV. NO.: 1 DECEMBER 2023 | 4 PREPARED BY | SIGNATURE: ………………………… | KRISHAN LAL | SR. MGRBMD | 5 CHECKED BY | RITESH KUMAR | SR MGR BMD | 6 REVIEWED BY | OM PRAKASH | MATHEW EIPE KOVOOR | DHURJATI PRASAD PATRA | 8 APPROVED FOR ISSUE | SANJAY KUMAR SINHA | 9 DATE OF ISSUE | 10 INDEX LIST ENCLOSED | 11 CHECKLIST ENCLOSED | 12 DISTRIBUTION LIST ENCLOSED | 13 C2 FORM ENCLOSED | 566909 | 202317:23:48 | 17:23:48 | D13 | SUBJECT:REVISION OF LMI PREVENTION AND DETECTION OF GENERATOR ROTOR EARBTH FAULTS | 007 O | MINOR CHANGES WERE MADE INLINE WITH COS DOCUMENT AND REVISION DOCUMENT "LMI ON GENERATOR ROTOR EARTH | FAULTS_REVISED.PDF" IS PUT UP FOR REVIEW. | APPROVAL OF COMPETENT AUTHORITY PLEASE. | SUBMITTED FOR REVIEW | जॉनसन प्रसन्ना कुमार कालाड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ासी विरष्ठ प्रबंधक | JOHNSON PRASANNA KUMAR KALADASI 101844 SENIOR MANAGER | 9437018478 | PRASANNAKUMAR01@NTPC.CO.IN | 09:39:12 | 10:55:42 | REVIEWN AS DISCUSSED | 09:32:12 | SIR | AS DNISCUSSED REVIEWED AND MODIFIED. | जॉनसन प्रसन्ना कुमार कालाड़़़ासी विरष्ठ प्रबंधक | 20:06:36 | LMI REVNIEWED | REVISED AND CHECK LIST INCORPORATED | 19:01:52 | 16:34:04 | 17:35:37 | PL REVIENW AND FORWARD FURTHER FOR APPROVAL | 18:59:26 | PROPOSEND LMI IS REVIEWED AND FOUND IN LINE WITH OGN. | 18:16:39 | PLEASE CNONSIDER THE FOLLOWING CHANGES: | • CHANGE THE SHEET NO.1 WHERE IT IS MENTIONED "IMPLEMENTATION BY ………….………………… | SHEET NO. 7 OF THE REVISED LMI IN CLAUSE NO. 12. PLEASE CONSIDER REPLACING THE OLD | • ON PAGE NO. | 20:06:54 | 18:06:49 | REQUIREND CHANGES AS MENTIONED IN EARLIER NOTE PAGES WAS DONE AND NEW FILE ATTACHED AS LMI PREVENTION AND | DETECTION OF GENERATOR ROTOR EARTH FAULTS_181123.PDF. | PUT UP FOR REVIEW AND APPROVAL PLEASE. | 19:04:21 | 09:42:53 | MODIFIEND AND REVIEWED | 17:33:43 | REVISEDN AS PER THE OBSERVATION MADE BY GM MAINTENACE | MAY BE APPROVED. | 13:35:05 | 16:56:32 | 18:44:25 | PAGE 1 OF 8 | OCT 2023 | ISSUE: 1 | REVISION:4 | 007 | SIMHADRI THERMAL POWER STATION | LOCAL MANAGEMENT INSTRUCTION | REVISION : 4 | PREVENTION AND DETECTION OF GENERATOR | ROTOR EARTH FAULTS | IMPLEMENTATION BY_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | PAGE 2 OF 8 | NTPC LTD. | LMINAME : PREVENTION AND DETECTION OF GENERATOR | ISSUE NO. 1 REVISION : 4 DATE :OCT 2023 | DESIGNATION SIGNATURE AND NAME | PREPARED BY SR MANAGER EM | CHECKED BY EM | 373812 | 202317:13:28 | 17:13:28 | SUBJECT:LMI REVISION LMI | 19DISSOLVED GAS ANALYSBIS OF | REACTORS O | TRANSFORMERS | LMI REFERENCE NO:LMI | CHANGES ENVISAGED BY COS . LMI HAS BEEN CHECKED AND REVIEWED FOR LATEST UPDATES AND CHECKLIST AS PER | LATEST OGN . | PUT UP APPROVAL OF COMPETENET AUTHORITY PLEASE. | 18:44:32 | 18:12:41 | 16:27:17 | 16:29:17 | LMI RENVIEWED WITH RESPECT TO OGN | FOUND IN ORDER. | 16:34:06 | FORWARNDED FOR APPROVAL. | 16:46:32 | LMI REVNISION MAY PLEASE BE ACCORDED KIND APPROVAL BY C.A. | 12:27:29 | 15:32:09 | 20:50:41 | 12:51:20 | REACTORS | DISSOLVED GAS ANALYSIS OF TRANSFORMERS | SIMHADRI SUPER THERMAL POWER PLANT | REVISION NO.: 02 | REVIEWED ON 07.08.2023 AND NO REVISION IN LINE WITH CCOS | IMPLEMENTATION _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | CGM SIMHADRI | SIMHADRI THERMAL POWER PLANT | LMI NAME : DISSOLVED GAS ANALYSIS OF TRANSFORMERS | 019 | ISSUE NO. : 1 R E V ISION : 2 DATE : AUGUST 2023 | PREPARED BY SATISH KUMAR SINGH DGM EM | REVIEWED BY DHARMENDRA KUMAR TOMAR AGM EM | REVIEWED BY MATHEW EIPE KOVOOR GM M | REVIEWED BY DHURJATI PRASAD PATRA GM O | APPROVED BY SANJAY KUMAR SINHA GGM | 1.0 INTRODUCTION 1 | 2.0 SUPERSEDED DOCUMENT 1 | 3.0 RECORDS OF REVISION 1 | 4.0 REFERENCE DOCUMENT 1 | 5.0 SCOPE 2 | 6.0 GUIDELINES 2 | 6.01 GUIDELINES REGARDING OIL SAMPLING FREQUENCY FOR DGA | OF TRANSFORMERS AND REACTORS 2 | 6.02 GUIDELINES FOR STUDY AND INTERPRETATION OF DGA RESULTS 3 | 6.03 GUIDELINES REGARDING ONLINE DGA MONITORING | OF GENERATOR TRANSFORMER 3 | 6.04 INFORMATION AND GUIDELINE FOR DGA RESULTS IN SAP 3 | 6.05 GUIDELINES REGARDING DGA FACILITY AT SITE 4 | 6.06 GUIDELINES OF INTERPRETATION OF FAULT GASES 4 | 6.07 GUIDELINE ON TRANSFORMER OIL AGING PARAMETER TESTING. 15 | 7.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED 16 | DISPENSATION OF DEVIATION 16 | 10.0 RECORD KEEPING 16 | 11.0 REVIEW 16 | DISSOLVED GAS ANALYSIS DGA IS A DIAGNOSTIC TECHNIQUE IN WHICH BY MONITORING THE TREND | DGA | OF VARIOUS FAULT GASES IN TRANSFORMERS AND REACTORS OIL | INTERPRETATION OF INCIPIENT FAULTS IN | THESE EQUIPMENTS CAN BE MADE. FOR THIS THE OIL SAMPLING FOR DGA HAS TO BE DONE ON | REGULAR BASIS. THERE ARE MANY NATIONAL AND INTERNATIONAL STANDARDS AND PRACTICES FOR | INTERPRETATION FOR DISSOLVED GAS RESULTS BASED ON WHICH THE GUIDELINES HAVE BEEN PREPARED | AND DESCRIBED IN SUBSEQUENT PARAGRAPHS. | THE GUIDELINES GIVEN IN THIS DOCUMENT ARE FOR A OIL SAMPLING FREQUENCY FOR CARRYING OUT | REACTORS AND B THE MET FOR INTERPRETATION OF THE | FAULT GASES FOUND DISSOLVED IN OIL. | 2.0 SUPERSEDED DOCUMENT | DECEMBER 2019 | 1 COSISO00OGN | 2 IEEE STD C571042008 | 3 IEC – 60599: 2015 | NTPC LTD SIMHADRI SUPER THERMAL POWER STATION PAGE 1 | 5.0 SCOPE : | GUIDELINES ARE GIVEN IN THIS DOCUMENT REGARDING OIL SAMPLING FREQUENCY FOR CARRYING OUT | DGA. THEY ARE APPLICABLE FOR FOLLOWING TRANSFORMERS AT SIMHADRI: | I. GT : 1R | II. SPARE GT STAGE #1 | III. 400 | 11 KV S | B TRANSFORMER STAGE #1 | IV. UNIT TRANSFORMER 1A | V. UNIT AUX. TRANSFORMER 1A | VI. REACTOR | VII. 11 | 33 KV MST – A | VIII. 33 | 11 KV SEA WATER TRANSFORMERS. | 0.415 KV ASH WATER RECIRCULATION TRANSFORMERS. | IX. 33 | 0.415 KV SWEET WATER TRANSFORMERS | X. 33 | XI. LT OUTDOOR SERVICE TRANSFORMER | 6.0 GUIDELINES | 6.01 GUIDELINES REGARDING OIL SAMPLING FREQUENCY FOR DGA OF TRANSFORMERS AND REACTORS: | REACTORS. | A TRANSFORMERS | 33 KV AND ABOVE | REACTORS 33 KV AND ABOVE | UNIT TRANSFORMERS: | 1ST SAMPLE JUST PRIOR TO CHARGING | 2ND SAMPLE – WITHIN 24HRS TO 48HRS OF CHARGING | CONTINUES 3 MONTHLY FOR GENERATOR TRANSFORMERS AND 6 MONTHLY FOR OTHER | NOTE: | OIL SAMPLES OF THE TRANSFORMERS AND REACTORS TO BE SENT TO NETRA WITH ABOVE SCHEDULE | FOR DGA.OIL SAMPLE OF THESE TRANSFORMERS AND REACTORS ARE TO BE TESTED WITH ONE MONTH | FREQUENCY AT SITE OR BY OUT SOURCING IF DGA KIT IS NOT AVAILABLE AT SITE. DEVIATED DGA | RESULTS ARE TO BE FORWARDED TO CCOS FOR REVIEW AND FURTHER ADVICE. | NTPC LTD SIMHADRI SUPER THERMAL POWER STATION PAGE 2 | 816829 | 202213:14:29 | 13:14:29 | D24 | BUILDBINGS IN | THE VICINITY OF CORROSIVE CHEMICALS | EFFLUENTS AND FUMES O | BUILDINGS IN THE VICINITY OF CORROSIVE | REV. NO.2 WAS PREPARED AND | EFFLUENTS AND FUMES" WITH REF. LMI | CHEMICALS | 012 | APPROVED IN THE MONTH OF JAN'2020. | THE LMI HAS BEEN REVIEWED AS ON DATE AND NO CHANGES ARE ENVISAGED. | पांडब दत्ता विरष्ठ प्रबंधक | PANDAB DATTA 102082 SENIOR MANAGER | PANDABDUTTA@NTPC.CO.IN | 9435483347 | BUILDINGS IN THE VICINITY OF CORROSIVE CHEMICALS | REV. NO.3 MAY PLEASE BE APPROVED. | 09:50:11 | LMI MANY PLEASE BE APPROVED. | 13:39:05 | 13:43:11 | PLEASE RNEVIEW ENTRIES ON PAGE NO.2 OF THE REVISED DOCUMENT GIVEN IN ANNEXURE AS DISCUSSED. | GIVEN IN ANNEXURE | 13:42:37 | PAGE NNO.2 MODIFIED AS DISCUSSED. | 18:30:49 | 13:06:15 | 09:27:27 | DIWAKAR KAUSHIK 004463 CHIEF GENERAL MANAGER | 9650992683 | DIWAKARKAUSHIK@NTPC.CO.IN | 16:42:33 | ISSUE NO.1; REVISION NO.:03; FEB’2022 | EFFLUENTS AND FUMES | IMPLEMENTATION ................................................................ | CGM | DATE :.................................... | 1. TITLE OF LMI BUILDINGS IN THE VICINITY OF CORROSIVE | DATE ISSUE NO.1; REVISION NO.: 03; FEB’2022 | ONG | REV. 02 | JAN’2020 | NAME: SHRI. PANDAB DATTA | 4. PREPARED BY | SR. MGR. O | NAME: SHRI. J. GOPIKIRAN | 5. CHECKED BY | NAME: SHRI. A. K. MUKHOPADHYAY | NAME: SHRI. M. E. KOVOOR | 6. REVIEWED BY | NAME: SHRI. G. C. CHOUKSE | NAME: SHRI. DIWAKAR KAUSHIK | 7. APROVED BY | 8. DATE OF ISSUE | 9. INDIX LIST ENCLOSED | REV: 3.00 DATE: FEB’2022 | 012 PAGE: 01 OF 09 | 7.0 METOLOGY OF PAINTINGS 45 | 8.0 EXCEPTION REPORTING 6 | 10.0 RECORD KEEPING 6 | 11.0 REVIEW 6 | 12.0 REVISION INDEX 7 | 13.0 DISTRIBUTION LIST 8 | 14.0 COMPLIANCE RECORD 9 | EFFLUENTS AND FUMES. | 012 PAGE: 02 OF 09 | ALKALINE HANDLING AREAS IN SIMHADRI POWER PROJECT. LIKE DM PLANT BUILDING NEUTRALIZATION | THE ACID | ALUM AND ACIDS SODIUM CHLORIDES AND BATTERY ROOMS ARE LINED WITH ACID | STORAGE AREA OF LIME | PITS | RESISTANT TILES | BIT MASTIC COATINGS | AND EPOXY PLANTS AS BARRIER IN BETWEEN CONCRETE SURFACES AND | CHEMICALS. THE CONCRETE SURFACES IF CONTRACTED WITH THE ACIDS AND CHLORIDES WILL BE | AFFECTED | CORRODED. THERE BY THE REINFORCEMENT BARS WILL BE EXPOSED AND THE REINFORCEMENT TOO WILL | BE CORRODED | ULTIMATELY THE STRUCTURE WILL BE COLLAPSE. THE FUMES OF THE ACIDS ALSO AFFECT THE | WINDOWS STEEL PLASTERING OF WALLS AND STRUCTURAL STEEL MEMBERS. FOR SMOOTH AND UNINTERRUPTED | STEEL | ACID HANDLING AREAS ARE TO BE SAFE AND | POWER GENERATION THE SAFETY OF THE STRUCTURES AND BUILDINGS | ALKALI PROOF LINING IN | INTACT AND THIS CAN BE ACHIEVED BY PERIODICAL INSPECTION AND MARINATING THE ACID | GOOD CONDITION. THE OBJECTIVE OF THIS LMI IS TO INSTRUCT AND MONITOR THE MEASURES TO BE TAKEN FOR | INSPECTION OF THE BUILDINGS AND THE STRUCTURES IN THE VICINITY OF THE ACIDS AND ALKALINE HANDLING AREA. | REGENERATION AREA | COATINGS AT NTPC | EFFLUENT TRENCHES | SIMHADRI. THE VARIOUS ARE LIKE DM PLANT | PIT | NEUTRALIZATION | CHEMICAL STORES AREA | CHEMICAL HOUSE | AREA AROUND EQUIPMENTS | FOUNDATIONS | SALT STORING | ALKALI STORE AREA | BATTERY ROOMS | CHEMICAL LAB AREA | ALUM SOLUTION PREPARATION TANK | ACID | CW CHLORINATION BLDG | AREA | ETP | TANKS | PLATFORMS | PUMP HOUSES | OIL | OIL SPILLAGE AREA LIKE OIL CANNELS | STORAGE ROOMS | COT | CPU | STRUCTURES ON CLARIFIERS | DOT ETC. | GRAVITY FILTERS AND IN THE OF NDCT ETC. | 4.0 REFERENCE DOCUMENT: | CORPORATE CENTER IS2395 | IS1475 | 5.0 SUPERSEDED DOCUMENT: | NONE | PAGE: 03 OF 09 | CAUSE FAILURE MEASURES | TILE LINING | 1.0 BRICK | 1.FREQUENCY OF 1.THROUGH 1.ALL INSPECTION OF | 1.1 JOINTING LOOSE BAND | EXCEPTIONAL | INSPECTION EVERY WASHING CLEANING | REFILL REPORTS ANNXIII | ANNX-III | MORTAR DISINTEGRATION YEAR EXCEPT FOR CHISELING | ALONG CORROSIVE ALUM | CHEMICALS TO WHERE IN ITS ONCE IN OF SAME QUALITY 2. TESTING BY | CRACKED BRICK | TILE 3. EXECUTION OF | 2.SURFACE CLEANING | VISUAL INSPECTION OF 3.INJECTION REPAIR | REPLACEME | JOINTS | LINING FOR GROUTING FOR NT BY CIVIL MAINT. | DESALTING | DEPENDING OF | CRACKS | 1.2 BEDDING LOOSE BOND IN AND MAGNIFICATION OR LINING | HANDLE MICROSCOPE 4.RELINING WITH | BEDDING MORTAR | MORTAR FALL IN VERTICAL LINING 3.LINING FOR EPOXY MORTAR AS | HOLLOWNESS OF THE PER REQUIREMENT | 1.3 BRICKS | TILES CRACKS | DEFECTIVE BENDING BUT MAINTAIN AT | 4.PAINTING SURFACES LEAST 0.5M WATER | ACCIDENTAL DAMAGE SHALL BE INSPECTED LEVEL FROM BOTTOM | ALLOWING SEEPAGE ONCE IN EVERY SIX OF BASKET TO | OF HARMFUL MONTHS REDUCE IMPACT | CHEMICALS 5.IF REQUIRED 5.FOR CONCRETE | CONCRETE SAMPLES TO SURFACE FOLLOW | 2.0 EPOXY LINING COLD JOINTS | P-II | IN CHEM. LAB FOR OF IS 2395PII CL | PINHOLES CRACKS | CHLORIDE ETC. 4.3 GIVEN ANNEXI | STRUCTURAL | 6. FOR STEEL | DEFORMATION | SURFACES FOLLOW IS | CHEMICALS WEATHER | 1477PII CL.7 | ETC. | GIVEN ANNEXII | 3.0 BITUMEN LINING | 4.0 EPOXY BLISTERING DUE TO | CHEMICAL ENTRAPPED AIR | PAINTING | RESISTANT CHEMICALLY EFFECT | PEELING | RUSTING | 316965 | 202417:39:44 | 17:39:44 | FOUNDATIONS INCLUDING SPRING SUPPORTED FOUNDATIONS WITH REF. B | SUB : REVIEW OF LMI MANUAL FOR INSPECTION | SUPPORTED FOUNDATIONS WITH REF.LMI | 011 | THE LMI OF "MANUAL FOR INSPECTION | REV. NO.5 WAS PREPARED AND APPROVED IN THE MONTH OF | FOUNDATIONS" WITH REF. LMI | FEB'2022. | चन्द्र शेखर गोडी उप महाप्रबंधक | CHANDRA SEKHAR GODI 085565 DY. GENERAL MANAGER | CSGODI@NTPC.CO.IN | 8332862038 | CHECKEND AND FORWARDED FOR APPROVAL. | 17:49:04 | 17:57:03 | IT IS REQNUESTED TO MODIFY AS PER STANDARD FORMAT OF SIMHADRI LMI GUIDELINES FOR ISSUE OF LMIS AS A | CONTROLLED DOCUMENT LMI | BE ADDED | 18:15:07 | LMI IS NPREPARED AS PER STANDARD FORMAT OF SIMHADRI LMI. CHECKLIST ADDED. REVISED LMI ATTACHED. | THE LIST OF MODIFICATIONS IN THE LMI REVISION ARE AS UNDER: | 1. FOLLOWING IS ADDED AT THE END OF CLAUSE 7 II INLINE WITH REVISION A IN OGN REV.01 MAY 2024: | “STATION MUST HAVE | ASSESS INSITU STRAIN MEASUREMENT.” | 2. REVISION B IN OGN REV.01 MAY 2024 REGARDING TG BENCHMARK READING OF SUPERCRITICAL UNITS IS NOT | ADDED AS THE SAME IS APPLICABLE FOR 660 | 800MW UNITS AND NOT FOR 500MW UNITS AT SIMHADRI. | 4. CHECKLIST | APPENDIXI VIBRATION TROUBLESHOOTING CHART AND APPENDIX II PROCEDURE FOR INSITU | VIBRATION TROUBLESHOOTING CHART | LMI IS SUBMITTED FOR APPROVAL PLEASE. | 19:02:46 | 08:39:32 | 16:50:43 | REVIEWNED. FOUND IN ORDER. | 17:12:59 | 17:38:11 | 16:06:53 | 10:24:09 | LMI REVNIEWED AND NO CHANGES PROPOSED. | FORWARDED FOR APPROVAL. | 18:52:11 | 16:49:32 | 17:22:33 | 13:08:30 | FORWARNDED FOR FURTHER APPROVAL | आगे की स्वीकृित के िलए भेजा गया | 10:06:27 | 11:24:26 | INCLUDING SPRING SUPPORTED FOUNDATIONS | REVISION NO.:06; JULY’2024 | APPROVED FOR IMPLEMENTATION BY HOP SIMHADRI | LMIDC S | 824003 | 202519:14:47 | D04 | 19:14:47 | MANAGEMENT OF DC SUPPLY SYSTEM FAILURE | MANAGEMENT OF DC SUPPLY SYSTEM FAILURE O | 002 MANAGEMENT OF DC SUPPLY SYSTEM FAILURE IS | 3RD REVISION OF LMI | PROPOSED THROUGH THIS NOTE. | LMI PAGE NOS. ARE REVIEWED AND CORRECTED AS PER EXTERNAL LMI AUDIT OBSERVATION. | I IS REQUESTED TO REVIEW THE PROPOSED REVISION OF THE LMI. | PUT UP FOR FURTHER REVIEW AND APPROVAL. | राजन्े द्र िसह उप महाप्रबंधक | RAJENDRA SINGH 062078 DY. GENERAL MANAGER | 9650995459 | RAJENDRASINGH@NTPC.CO.IN | CHECKEND THE DOCUEMNT. MAY PLEASE APPROVE. | मेड़़ा नाग राजा उप महाप्रबंधक | 08:48:19 | 10:17:56 | PLEASE ANDD LMI CHECK LIST AS ANNEXURE AS LAST PART OF LMI | 10:56:44 | LMI CHNECK LIST IS ADDED AS ANNEXURE. PLEASE PROCESS. | 20:07:42 | 12:04:31 | REVIEWND AS DISCUSSED. | 18:49:03 | 17:25:45 | 12:00:43 | MAY PL NREVIEW THE LMI | 15:53:30 | 17:33:17 | FORWARNDED FOR APPROVAL AFTER REVIEW | 09:42:18 | सोमनाथ भट्टाचायर् अपर महाप्रबंधक | SOMNATH BHATTACHARYA 007203 ADDL. GENERAL MANAGER | 9431600725 | SOMNATHBHATTACHARYA@NTPC.CO.IN | 17:40:54 | PROPOSEND LMI IS REVIEWED AND FOUND IN LINE WITH OD. | 10:50:45 | CHECKEND AND FORWARDED. | 16:21:41 | 17:34:56 | 16:26:16 | MAY PLNEASE BE APPROVED. | प्रसन्ता कुमार जेना महाप्रबंधक | PRASANTA KUMAR JENA 006081 GENERAL MANAGER | 9650990836 | PKJENA@NTPC.CO.IN | 13:15:26 | समीर शमार् मख्ु य महाप्रबंधक | SAMEER SHARMA 005041 CGM | SAMEERSHARMA@NTPC.CO.IN | 9650990022 | 19:47:43 | 835333 | 202212:40:07 | D02 | 12:40:07 | SUBJECT:LMI REVEIEW OF INSPECTION OF STORM WATER DRABINS IN | PLANT AREA. O | THE LMI INSPECTION OF STORM WATER DRAINS IN PLANT AREA W.R.T REF.NO.: | HAS BEEN REVIEWED AND NO CHANGES. | सत्यनारायण पी वी राजू प्रबंधक | PALAPARTHI VENKATA SATYANARAYANA RAJU 007476 MANAGER | 9440918617 | PVSATYANARAYANARAJU@NTPC.CO.IN | THE LMNI OF "INSPECTION OF STORM WATER DRAINS IN PLANT AREA" WITH REF. LMI | REV. NO.3 | ATTACHED MAY PLEASE BE APPROVED FOR IMPLEMENTATION. | ATTACHED | 19:17:45 | LMI MANY PLEASE BE APPROVED | 09:10:53 | SUBMITNTED FOR APPROVAL OF COMPETANT AUTHORITY | 09:22:06 | 20:26:56 | 10:26:09 | 11:11:53 | ISSUE NO.:1 | REV: 03 DATE: FEB’2022 | PPPPLLLLAAAANNNNTTTT AAAARRRREEEEAAAA.... | INSPECTION OF STORM WATER DRAINS IN | 1. TITLE OF LMI | PLANT AREA | DATE ISSUE NO.1 | REVISION NO.: 03; FEB’2022 | NAME: SHRI. P.V.S.N. RAJU | MGR. O | NAME: SHRI. J. GOPI KIRAN | TITLE: INSPECTION OF STORM WATER DRAINS IN PLANT AREA. | PAGE: 01 OF 06 | 2.0 SCOPE 1 | 3.0 REFERENCE DOCUMENT 1 | 4.0 SUPERSEDED DOCUMENT 1 | 5.0 SPECIFIC INSTRUCTIONS 2 | 7.0 EXCEPTION REPORTING 3 | 9.0 RECORD KEEPING 3 | 10.0 REVIEW 3 | 1.0 INTRODUCTION: | STORM WATER DRAINS IN SIMHADRI ARE DESIGNED AND CONSTRUCTED TO DISPOSE OF 1 RAIN WATER IN THE | CATCHMENT OF OUTSIDE PERIPHERY AND 2 RAIN WATER IN THE CATCHMENT OF PLANT AREA AND USED | WATER FROM PLANT BUILDINGS ETC. PERIPHERAL DRAINS WERE CONSTRUCTED TO DIVERT THE EXISTING NALLAHS | WHICH ARE FLOWING ACROSS THE PLANT LOCATION ON FOUR SIDES OF THE PLANT BOUNDARY WALL WITH AN | OBJECTIVE THAT THE RAIN WATER OF OUTSIDE CATCHMENT AREA SHALL NOT ENTER PLANT PREMISES AND IT | SHOULD BE DISPOSED OFF IN TO SEA. STORM WATER DRAINS WERE CONSTRUCTED ALL ALONG THE ROADS OF | PLANT AREA TO DISPOSE OFF THE RAINWATER AS WELL AS WASH WATER. THE DRAINS WERE CONSTRUCTED WITH | RCC IN RECTANGULAR SECTIONS. THE BED SLOPE WAS PROVIDED AS 1 IN 1000. ALL THE DRAINS AT BOUNDARY | WALL WERE PROVIDED WITH VERTICAL GRILLS MADE WITH GI PIPES TO PREVENT ENTRY OF CATTLE OR PERSONS | THROUGH THESE OPENINGS. TO AVOID CONSEQUENTIAL DAMAGES. | THE SCOPE OF THIS LMI IS TO DETAIL THE METS THAT ARE TO BE ADOPTED FOR THE INSPECTION AND | OPERATING GUIDANCE NOTE NO.OGN | REV.00 | 4.0 SUPERSEDED DOCUMENT: REF: LMI | 5.0 SPECIFIC INSTRUCTIONS: | THE FOLLOWING CHECKS ARE TO BE CONDUCTED PERIODICALLY ON THE ACID | ALKALI PROOF LININGS | PAINTINGS | FOR THE SAFETY AND LONGEVITY OF STRUCTURES AND BUILDINGS | ALKALI LININGS BY VISUAL INSPECTION. | A CHECKING OF ACID | STEEL STRUCTURES AND CHEMICAL ACTION ON CONCRETE | B CHECKING FOR CORROSION OF REINFORCEMENT | CEMENT WORKS | C CHECKING FOR CONDITION OF WELDS OF JOINTS OF STEEL MEMBERS | D CHECKING OF CONDITION OF PAINTS OF STRUCTURES | E VISUAL INSPECTION OF RCC DRAINS FOR CORROSION AT THE DRAINS SITUATED AT DM PLAN | F STORM WATER DRAINS INSPECTION IS TO BE DONE WELL BEFORE MONSOON. THIS WILL BE INCLUDED IN | PREMONSOON ACTION PLAN REVIEW. | PAGE: 02 OF 06 | THE INSPECTION SHALL BE CARRIED OUT IN THE MONTHS OF MAY | JUNE EVERY YEAR BY INSPECTION | VISUAL INSPECTION: | A. THE PERIPHERAL DRAINS ARE TO BE INSPECTED VISUALLY FOR ANY SETTLEMENTS IN | STONE PITCHING IN THE BED AND SLOPE. | DRAINS INSIDE THE PLANT AREA ARE TO BE INSPECTED FOR | B. THE PERIPHERAL DRAIN | VEGETATION GROWTH. | C. VISUAL INSPECTION IS TO BE CARRIED OUT FOR SILTING AND INSTRUCTIONS OF FLOW IN THE | DRAINS. | D. VISUAL INSPECTION IS TO BE CARRIED OUT FOR ANY CORROSION OF REINFORCEMENT DUE | TO CHEMICAL REACTIONS OF ACIDS | ALKALINE WHICH ARE LET OUT IN TO DRAINS. | E. VISUALS INSPECTION FOR ANY CHEMICAL ACTION ON CONCRETE SURFACE DUE TO FLOW OF | CHEMICALS IN TO DRAINS. | F. VISUAL INSPECTION IS TO BE CARRIED OUT FOR EFFECTIVE WORKING OF GRILLS PROVIDED | IN THE DRAINS AND FOR ANY CORROSION OR PHYSICAL DAMAGES TO THE GRILLS. | G. VISUAL INSPECTION IS TO BE CARRIED OUT FOR THE BLOCKAGES IN THE OUTFALL DRAINS | BLOCKAGES OF OPENINGS WITH LEAVES | GUNNY BAGS STONES OR EACH. | H. VISUAL INSPECTION IS TO BE CARRIED OUT FOR BLOCKAGES IN THE OUTFALL DRAINS. | PAGE: 03 OF 06 | 7.0 EXCEPTION REPORTING | THE EXCEPTIONS ENCOUNTERED DURING INSPECTION ARE TO BE REPORTED AS PER THE FOLLOWING FORMAT BY THE | DESCRIPTION OF WORK UNIT NO LOCATION OF EXCEPTION REMARKS | CHP | 9.0 RECORD KEEPING | THE RECORDS TO BE MAINTAINED UNDER THE LMI INCLUDE | A COMPLIANCE RECORD OF THE ACTIVATE DETAILED UNDER THIS LMI | B REPORTS OF INSPECTION CARRIED OUT | C EXCEPTION IN REPORTING | THE ABOVE RECORDS ARE TO BE MAINTAINED BY O | MCIVIL FOR RELEVANT RESPONSIBILITIES. | 10.0 REVIEW | THIS DOCUMENT SHALL BE RECEIVED BY HOP OF SIMHADRI ON TWO YEARLY BASIS. | 11:28:33 | 196416 IDATE:04 | LMI 243 | 202511:28:33 | SUBJECT:REVISION OF LMI FOR WATER AUDIT O | 034 | LMI IS REVISED ON THE BASIS OF COSISO00OGN | 034 REV. NO.: 2 MAR 2025. | नीरज कुमार िसह विरष्ठ प्रबंधक | NEERAJ KUMAR SINGH 103459 SENIOR MANAGER | 9471007277 | NKSINGH10@NTPC.CO.IN | 196416 | 16:09:45 | LMI HANS BEEN REVISED ON THE BASIS OF REVISED OGN DATED 02 | 2025. | REVISED LMI IS IN LINE WITH THE REVISED OGN. | 18:27:02 | 19:51:06 | समीर शमार् कायर्कारी िनदेशक | SAMEER SHARMA 005041 EXECUTIVE DIRECTOR | EXECUTIVE DIRECTOR | 20:00:43 | WATER AUDIT | 034 REV: 03 | MAY2025 | 1 LMI NAME WATER AUDIT | 3 COSISO00OGN | 034 REV. NO.: 2 | MAR 2025 | SUPERSEDED DOCUMENT | 034 REV 2 DT. MARCH | 2023 | NAME: NEERAJ KUMAR SINGH | NAME: NAVIN KISHORE | NAME: P. K JENA | 8 APPROVED BY NAME: SAMEER SHARMA | 2.0 SUPERSEDED DOCUMENTS 2 | 3.0 DETAILS OF REVISION 2 | 4.0 OBJECTIVE 2 | 5.0 FREQUENCY 2 | 6.0 SCOPE OF AUDIT AND METOLOGY 23 | 9.0 REVIEW 3 | 10.0 ANNEXURE 45 | 11.0 CHECKLIST 69 | TITLE WATER AUDIT | LARGE VOLUMES OF WATER IS USED IN VARIOUS | A POWER STATION IS WATER EXTENSIVE INDUSTRY | APPLICATIONS AS DISCUSSED BELOW. | AT NTPC SIMHADRI | WATER REQUIRED FOR STEAM COOLING IN CONDENSER IS MET BY WATER TAKEN | FROM SEA BAY OF BENGAL USING 3 NOS OF PUMPS HAVING RATED FLOW OF 9000 CU.M | HR. AT A | BAY OF BENGAL | TOTAL OF 40.3 MWC. THIS SEA WATER IS ALSO USED FOR WET DISPOSAL OF BOTTOM ASH IN ASH | SLURRY PUMP HOUSE. THE WATER USED IN MAKING ASH SLURRY AND TRANSPORTATION OF THIS SLURRY | TO ASH DYKE IS DECANTED IN THE ASH DYKE WELLS AND IS RECIRCULATED AGAIN TO THE ASH WATER | PUMP HOUSE USING ASH WATER RECIRCULATION PUMPS. A PART OF THE RE CIRCULATED WATER IS SENT | TO EDP EFFLUENT DISCHARGE PUMP HOUSE WHERE | EFFLUENT DISCHARGE PUMP HOUSE | ALONG WITH BLOW DOWN WATER CW AND | CHP DRAIN IT IS PUMPED BACK INTO THE SEA. FLOW METERS ARE INSTALLED IN BOTH THE SEA WATER | INTAKE LINE WORKING AND STANDBY AND IN THE PIPELINE FROM EDP TO THE SEA. SEA WATER | WORKING AND STANDBY | SCHEME OF THE PLANT IS ENCLOSED AT ANNEXURE1. | FIRE WATER IS BEING MET BY SWEET WATER | WATER REQUIREMENT FOR OTHER PURPOSES LIKE PT PLANT | FROM YELERU CANAL. THE SAME IS PUMPED FROM SWEET WATER PUMP HOUSE STAGEI: 4 NOS | HR. AND 2 X 600 CU. MT | OF PUMPS: 2 X 750 CU.MT | HR. STAGE2: 3 NOS OF PUMPS: 1 X 600 | CU. MT | HR.. FROM HERE SWEET WATER IS PUMPED TO RAW WATER | HR. AND 2 X 750 CU.MT | RESERVOIR AS PER THE REQUIREMENT. THROUGH RAW WATER PUMPS S W E E T WATER SENT TO THE | PLANT REQUIREMENTS OF PT PLANT | FIRE WATER AND SERVICE WATER. THE SCHEME OF SWEET WATER | IS ENCLOSED AT ANNEXURE2. | WATER BEING A SCARCE RESOURCE ALL EFFORTS ARE MADE TO MINIMIZE THE CONSUMPTION OF WATER. | THIS OBJECTIVE IS ACHIEVED THROUGH PROPER SELECTION AND DESIGN OF POWER PLANT | SCHEMES | PRACTICES. | INEFFICIENT UTILIZATION OF | AUDIT OF WATER BALANCE SYSTEM ALSO HELPS IN IDENTIFYING THE WASTAGE | WATER. SUCH AUDITS COMPARE THE PRESENT FLOWS IN DIFFERENT WATER CIRCUITS AND COMPARE IT | WHICH HELP IN IDENTIFYING THE PROBLEMATIC AREAS | WITH THE DESIGNED FLOWS | SYSTEMS. THE | AUDITS ALSO SHOULD SUGGEST WATER CONSERVATION ACTION PLAN. | P AG E ¦ 1 | 034 REV 2 DT. FEB 2023 | 3.0 DETAILS OF REVISION | ENTIRE LMI HAS BEEN REVISED ACCORDING TO TC DOCUMENT REVISION. | 4.0 OBJECTIVE | 4.1 TO CARRY OUT THIRD PARTY WATER AUDIT AT SIMHADRI STATION IN A PREDETERMINED TIME FRAME. | AWRS | 4.2 SCOPE OF WORK SHOULD BE CLEARLY DEFINED INCLUDING USAGE OF STP | EXPLORING WAYS TO REDUCE EVAPORATION | LEAKAGES | WASTAGES SHOULD BE THE DELIVERABLE. | 4.3 REDUCING WATER CONSUMPTION BY ADOPTING DIFFERENT NEW TECHNOLOGIES SHOULD ALSO BE | SUGGESTED. APPROVAL OF LMI | 5.0 FREQUENCY | THIRD PARTY EXTERNAL AUDIT IS TO BE CARRIED OUT IN EVERY 3RD YEAR. STATION MUST CARRY AN | INTERNAL REVIEW OF THE WATER CONSUMPTION AND IMPLEMENTATION OF WATER AUDIT | THE STATIONS CARRY OUT THIRD PARTY WATER AUDIT AS PER FREQUENCY DECIDED ABOVE. | METOLOGY | 6.0 SCOPE OF AUDIT | 6.1 THE FOLLOWING AREAS NEED TO BE COVERED IN THE AUDIT: |  RAW WATER SYSTEM |  PT WATER SYSTEM |  CIRCULATING WATER CW AND COOLING TOWER CT SYSTEM |  CT BLOW DOWN | DRINKING WATER | SERVICE |  FIRE |  ASH SLURRY SYSTEM |  ASH WATER SYSTEM |  ASH DYKE AND WATER RESERVOIR EVAPORATION ASSESSMENT |  EFFLUENT TREATMENT SYSTEM ETP | P AG E ¦ 2 | STP |  SEWERAGE TREATMENT PLANT STP |  DRAINAGE SYSTEM |  ZERO LIQUID DISCHARGE ZLD | ZLD |  FGD SYSTEM |  TOWNSHIP CONSUMPTION INCLUDING HORTICULTURE |  RAIN WATER HARVESTING | 6.1 A WATER BALANCE DIAGRAM SHALL BE PREPARED WHICH WILL INCLUDE ALL | CONSUMPTION AND SOURCE POINTS. | 6.2 PORTABLE ULTRASONIC FLOW METERS ARE TO BE USED FOR FLOW MEASUREMENTS | WHEREVER POSSIBLE. IN CASES WHERE STATION FLOW METERS ARE ALREADY INSTALLED | A COMPARISON BETWEEN PREINSTALLED METER AND OFFLINE PORTABLE METER | SHOULD BE NOTED. WHERE IT IS NOT TECHNICALLY FEASIBLE TO USE ULTRASONIC | FLOWS ARE TO BE ESTIMATED FOLLOWING BEST INDUSTRY PRACTICE. | METERS | 6.3 CYCLE OF CONCENTRATION TO BE CHECKED AND EVALUATED WITH RESPECT TO | PRESCRIBED COC. | REDUCE | WATER CONSUMPTION. IT CAN ALSO SUGGEST SUCCESSIVE USE OF SAME WATER IN THE | PROCESS KEEPING ITS QUALITY IN MIND. IN CASE WHERE FRESH INVESTMENT IS | THE SAME SHOULD BE SUPPORTED WITH COST BENEFIT ANALYSIS. | 6.5 ASSESSMENT OF POWER CONSUMPTION OF MAKE UP WATER | RAW WATER AND AWRS | PUMP HOUSE IS TO BE DONE. | THIS LMI SHALL BE REVIEWED BY HOP SIMHADRI EVERY 2YRS OR AS AND | WHEN NECESSARY. | ANNEXUREI: SWEET WATER BALANCE DIAGRAM | ANNEXUREII: SEA WATER BALANCE DIAGRAM | ANNEXUREIII: CHECKLIST | P AG E ¦ 3 | ANNEXUREI SWEET WATER BALANCE DIAGRAM | PA GE ¦ 4 | ANNEXUREI SEA WATER BALANCE DIAGRAM | PA GE ¦ 5 | 449840 | SIMCHEM | 202519:53:04 | 19:53:04 | SUBJECT:LMI REVISION FOR CHEMICAL CONTROL OF THE WATERSTEAM CIBRCUITS OF | DRUM ONCE THROUGH TYPE BOILERS AND HRSG. O | 001 REV. NO.: 10 | PREVIOUS LMI VERSION: LMI | REV. NO.: 11 | PRESENT LMI VESRION: LMI | CHANGES IN LMI ARE BRIEFED IN THE BELOW. | AFTER CATION CONDUCTIVITY | 1. ‘ACC’ AFTER CATION CONDUCTIVITY HAS BEEN REPLACED WITH ‘CC’ CATION CONDUCTIVITY IN ALL PARAMETER | CATION CONDUCTIVITY | TABLES | AS THE ABBREVIATION ‘ACC’ IS USED FOR AIRCOOLED CONDENSER IN THIS TC DOCUMENT. | 2.UPDATED SEC. 5.3 NOTEA | NOTE-A | AS AND WHEN REQUIRED. | MAINTAIN THE PH OF THE STEAMWATER CIRCUIT | 4.THE DM MAKEUP CC ANALYSER HAS BEEN REMOVED FROM THE CORE PARAMETERS LIST FOR ALL UNIT TYPES. | 5.UPDATED CLAUSE 7.2 INCORPORATED LOWLEVEL CHLORIDE UNDER DIAGNOSTIC MONITORING PARAMETERS | 6. UPDATED CLAUSE 8.1 TABLE2 INCORPORATED MONITORING OF TOC IN CONDENSATE WATER SAMPLES ALONG WITH | 7. UPDATED CLAUSE 8.3 TABLE4 INCORPORATED FEEDWATER SPECIFIC CONDUCTIVITY LIMITS FOR ALL TYPES OF UNITS. | FEEDWATER DO LIMIT HAS BEEN REVISED FOR BOTH MIXED METALLURGY AND ALLFERROUS UNITS. | 8. UPDATED CLAUSE 8.4 TABLE5. REVISED THE SPECIFIC CONDUCTIVITY LIMIT FOR DRUMTYPE UNITS. INCLUDED | WITH LIMITS FOR BOTH PPHATE AND CAUSTIC TREATMENT REGIMES. | MONITORING OF SODIUM IN BOILER WATER SAMPLES | 9. UPDATED ANNEXUREI INCORPORATED MONITORING OF SODIUM. | DRAFT LMI AND OD IS ATTACHED FOR REFERENCE. | आर. बालकृष्ण पट्नायक उप प्रबंधक रसायन | RBALAKRISHNAPATNAIK@NTPC.CO.IN | 9437494990 | सांतनु जेना उप महाप्रबंधक रसायन | 7458012612 | SANTANUJANA@NTPC.CO.IN | 09:32:06 | 10:44:04 | 18:22:37 | MODIFIEND ACCORDINGLY AND ATTACHED. | 11:16:11 | CLAUSE NNO. 11 TO BE REVISED IN LINE WITH SIMHADRI STATION LMI FORMAT | 12:09:05 | DOCUMNENT IS REVISED AND ATTACHED. MAY BE APPROVED. | 15:48:25 | 17:50:36 | LMI IS NIN LINE WITH THE OD. FORWARDED FOR FURTHER REVIEW. | 10:23:06 | सुिप्रितम कुरी उप महाप्रबंधक | SUPRATIM KURI 100946 DY. GENERAL MANAGER | SUPRATIM@NTPC.CO.IN | 9650998020 | 20:12:24 | FORWARNDED FOR FURTHER REVIEW PLEASE. | शिश कांत उप महाप्रबंधक | SHASHI KANT 101559 DY. GENERAL MANAGER | 19:48:42 | 20:24:31 | नीलांजन मंडल अपर महाप्रबंधक | 09:35:17 | LMI REVNIEWED AND IS IN LINE WITH THE REVISED OD. | के पी रमेश उप महाप्रबंधक | KANADE PIYUSH RAMESH 101897 DY. GENERAL MANAGER | 9425219272 | PIYUSHKANADE@NTPC.CO.IN | 16:08:27 | नीलांजन मंड़़़ल अपर महाप्रबंधक | 16:19:09 | 17:06:51 | LMI REVNIEWED. | अिनल कुमार मौयार् अपर महाप्रबंधक | ANIL KUMAR MAURYA 008631 ADDL. GENERAL MANAGER | 8004940574 | ANILKUMARMAURYA@NTPC.CO.IN | 09:34:19 | 11:52:44 | 11:00:19 | 17:17:02 | 17:37:40 | 460714 | OFC NOTE | D25 | 18:06:19 | 202518:06:19 | SUBJECT:LMI ON COOLING WATER TREATMENT MONITORING ABND | CHEMICAL CLEANING OF CONDENSER TUBES O | LOCATION MANAGEMENT INSTRUCTION ON COOLING WATER TREATMENT | MONITORING AND CHEMICAL CLEANING OF CONDENSER TUBES: | REVISION OF LMI LMI | 019 COOLING WATER TREATMENT MONITORING | AND CHEMICAL CLEANING OF CONDENSER TUBES: | THE SUBJECT LMI IS REVIEWED AND MADE BELOW MENTIONED CHANGES AS PER LATEST OGN. | FOLLOWING CHANGES HAVE BEEN DONE FROM PREVIOUS VERSION AS DESCRIBED BELOW: | SECTION 8.3: INHIBITOR SELECTION | 1. MODIFIED W.R.T. CHOICE OF INHIBITORS. | CRITERIA FOR CLEANING PROCESS. | INHIBITOR EFFICIENCY MODIFIED TO > | 2. SECTION 10.0: INHIBITOR EFFICIENCY | ALL METALLURGY. | 3. SECTION 11.1.3: ACID INJECTION CORROSION INHIBITOR CONCENTRATION MODIFIED. | 1. LMI IN WORD AND .PDF FORMATS. | 2. LATEST COSISO00OGN | JULY 2025 | 019 REV. NO.2 | 10:22:01 | 17:32:08 | 18:20:09 | LMI IS NIN LINE WITH THE OGN. FORWARDED FOR FURTHER REVIEW. | 13:02:38 | 16:03:32 | REVIEWNED AND FORWARDED. | 20:03:06 | REVIEWNED AND FORWARDED PLEASE. | 09:25:44 | 16:30:00 | LMI REVNIEWED AND IS IN LINE WITH THE OGN. FORWARDED FOR FURTHER REVIEW AND APPROVAL. | 16:00:57 | 16:19:05 | LMI IS NIN LINE WITH THE OGN. MAY PLEASE BE APPROVED. | 18:28:30 | 09:51:24 | 20:34:15 | 18:48:04 | COOLING WATER TREATMENT MONITORING AND | CHEMICAL CLEANING OF CONDENSER TUBES | 019 REV. NO.: 02 | DATED: OCT2025 | APPROVED FOR IMPLEMENTATION BY: HOP SIMHADRI | 1 LMI NAME COOLING WATER TREATMENT MONITORING | AND CHEMICAL CLEANING OF CONDENSER | TUBES | 3 REV. NO.:2 | JULY. 2025 | COSISO00GN | 4 REVISION: 01 JUNE23 | V. LALITHADEVI DY. MGR. CHEM | SANTANU JANA DGM | AHMAD KAUNAIN RAZA | 8 APPROVED BY SAMEER SHARMA | 87221 | D01 | 19:32:17 | 202419:32:17 | 002 REV:04 GUIDELINES FOR ISSUE OBF LMIS | SUBJECT:APPROVAL OF LMI | AS A CONTROLLED DOCUMENT O | 003 REV:04 "GUIDELINES FOR ISSUE OF LMIS AS A CONTROLLED DOCUMENT " HAS BEEN REVISED | .ENTIRE DOCUMENT IS REDRAFTED.LMI FORMAT IS MODIFIED. | MAY PLNS BE APPROVED | 08:40:56 | REVISIONNS IN LMI TO BE DETAILED IN NOTE FOR APPROVAL | 09:06:03 | PLS. ADDN THE DETAILS. | 09:50:42 | CLAUSE 5N TO 11 MODIFIED AS UNDER | UPLOADING ON LAN | CLAUSE 5:APROVAL OF LMI THROUGH PRADIP | CLAUSE 6.DIDISTRIBUTION OF LMI THROUGH LAN | CLAUSE 7:REVISION OF LMI BY CONCERNED | CLAUSE 8:CHANGE IN MASTER LIST AS A CONTROLLED DOCUMENT | CLAUSE 9:APPROVAL OF REVIEW BY HOP IN 2 YEARS OR EARLIER AS IT IS REQUIRED. | CLAUSE 10: INCLUSION OF CHECK LIST | LMI STANDARD FORMAT | CLAUSE 11 :INCLUSION OF ANNEXURE | 11:26:32 | CLAUSE 5 TO 11 ARE REVISED. LMI STANDARD FORMAT IS PREPARED. | LMI FONRMAT HAS BEEN REVISED | EACH LMI SHALL BE IDENTIFIED BY A SUITABLE TITLE AND UNIQUE NUMBER. REVISION NUMBER SHALL BE INDICATED AS | REV. NO.0 | REV. NO.1 … ETC. ISSUE DATE SHALL ALSO BE INDICATED. | 17:33:52 | MAY BEN APPROVED | 21:03:25 | PL ASK TNHE CONCERNED TO INDICATE THE CHANGES WRT TO EARLIER VERSION OF THE LMI IN THE BODY OF THE PROPOSAL | ITSELF. HENCEFORTH MAY BE DONE FOR ALL THE LMIS PROPOSED FOR REVISION. | SANJAY KUMAR SINHA 005185 CGM | 08:09:40 | DETAILS NOF REVISION IN LMI ARE GIVEN IN PAGE #3 OF NOTE. MAY KINDLY APPROVE | 18:01:01 | 18:14:40 | GUIDELINES FOR ISSUE OF LMIS AS A CONTROLLED D OCUMENT | 002 REV: 04 | MAY2024 | 1 LMI NAME GUIDELINES FOR ISSUE OF LMIS AS A CONTROLLED | 002 REV:04 | REV:01 | 3 COSISO00 OIN | MAY:2020 | 002 REV:03 APRIL 22 | NAME: U.S.VERMA | NAME: S.J.DAVID | 8 APPROVED BY NAME: S.K.SINHA | 2.0 SUPERSEDED DOCUMENTS 1 | 3.0 DETAILS OF REVISION 1 | 4.0 IDENTIFICATION 1 | 5.0 APPROVAL 1 | 6.0 DISTRIBUTION 1 | 7.0 REVISION 2 | 8.0 MASTER LIST 2 | 9.0 REVIEW 2 | 10.0 CHECKLIST 23 | 11.0 ANNEXURE 45 | TITLE GUIDELINES FOR ISSUE OF LMIS AS A CONTROLLED DOCUMENT | OBJECTIVE OF THE CONTROLLED ISSUE IS TO PRECLUDE USE OF INVALID AND | OR OBSOLETE DOCUMENTS. | A SYSTEM FOR CONTROLLED ISSUE SHALL BE IN PLACE FOR THE ABOVE PURPOSE AS ELABORATED IN THE | FOLLOWING PARAGRAPHS. | REV NO.3 DT: APRIL 2022 | THIS LMI FORMAT HAS BEEN REVISED. CLAUSE 5 TO 11 ARE REVISED. | 4.0 IDENTIFICATION OF LMI | EACH LMI SHALL BE IDENTIFIED BY A SUITABLE TITLE AND UNIQUE NUMBER. REVISION NUMBER SHALL | REV. NO.1 … ETC. ISSUE | BE INDICATED ALONG WITH THE DOCUMENT NUMBER AS REV. NO.0 | DATE SHALL ALSO BE INDICATED. | 5.0 APPROVAL OF LMI | 5.1 DOCUMENT SHALL BE REVIEWED AND APPROVED FOR ADEQUACY BY THE OF PROJECT PRIOR | TO ISSUE. THE APPROVAL OF THE DOCUMENT IS TO BE TAKEN THROUGH PRADIP. APPROVAL OF | THE DOCUMENT SHALL BE INDICATED ON THE FRONT SIDE OF THE DOCUMENT. | DOWNLOADED ELECTRONICALLY APPROVED LMI DOCUMENT CAN BE CONSIDERED AS MASTER COPY | OF THE DOCUMENT AND TO BE MAINTAINED BY THE ISSUING AUTHORITY. | 6.0 DISTRIBUTION OF LMI | PASSWORD PROTECTED | IS TO BE CONSIDERED AS CONTROLLED COPY. | PAGE ¦ 1 | 7.0 REVISION OF LMI | THE INITIATOR SHALL PUT UP FOR REVIEW | S IS FELT NECESSARY | 7.1 IF ANY CHANGE IN THE DOCUMENT | AND APPROVAL ALONG WITH THE DOCUMENT | S WITH PROPOSED CHANGES. THE REVISED | DOCUMENT IS REVIEWED AND APPROVED BY THE OF PROJECT. THE NEW REVISION NUMBER | AND THE ISSUE DATE SHALL BE INDICATED ON THE REVISED DOCUMENT. | CONCERNED | RESP. : CONCERNED | DOCUMENTS IS MADE AVAILABLE TO ALL USERS THROUGH LAN. THE OLD COPY SHALL BE REMOVED | FROM THE LAN AND THE REVISED LMI SHOULD BE UPLOADED. | 8.0 MASTER LIST | HAVING THE FOLLOWING | ISSUING AUTHORITY SHALL PREPARE AND MAINTAIN THE MASTER LIST | AS A MINIMUM: | COLUMNS | I SL. NO. | II DOCUMENT TITLE III DOCUMENT NO. IV LATEST REV. NO. | V DATE OF LATEST REVISION | MASTER LIST SHALL BE IDENTIFIED | DISTRIBUTED AND REVISED AS A CONTROLLED | THE MASTER LIST SHALL BE KEPT BY THE | AS DESCRIBED FROM 5 TO 7. HOWEVER | THE MASTER LIST SHALL ALSO NEED | ISSUING AUTHORITY. WHENEVER ANY LMI IS ISSUED OR REVISED | TO BE REVISED AND ISSUED. | 9.0 REVIEW | TAKE THE APPROVAL OF COMPETENT AUTHORITY HOP. THE | DOCUMENT WILL BE REVIEWED ON 2 YEARLY BASIS OR EARLIER | IF REQUIRED. | 10.0 CHECKLIST: AS ATTACHED | 11.0 ANNEXURE: LMI STANDARD FORMAT | PAGE ¦ 2 | 202216:22:14 | 33587 IDATE:13 | 16:22:14 | THE LOCATION MANAGEMENT INSTRUCTION LMI OF THERMAL PERFORMANCE OF COOLING TOWERS I.E. | 006 REVISION IS DONE ACCORDING TO THE EXTERNAL LMI AUDIT | EXCEPTION POINTS. | IN THIS LMI THE CALCULATION SHEET HAS BEEN CHANGED. | THE APPROVING AUTHORITY FOR LMI IS HOP. | 33587 | CHECKEND AND FOUND OK. | SUBMITTED FOR APPROVAL OF COMPETENT AUTHORITY | 17:57:00 | REVIEWEND AND SUBMITTED FOR APPROVAL | आई एल रेड्डी अपर महाप्रबंधक | ITIKYALA LAXMA REDDY 032235 ADDL. GENERAL MANAGER | 9440918055 | ILREDDY@NTPC.CO.IN | 20:07:28 | 07:21:59 | 16:56:57 | 9435483331 | SUBIRDEBNATH@NTPC.CO.IN | 11:13:00 | 11:37:05 | 19:46:32 | 15:44:41 | THERMAL PERFORMANCE OF COOLING TOWERS | REV:06 APR:2022 | TITLE THERMAL PERFORMANCE OF COOLING TOWERS AT NTPC SIMHADRI | 006 REV:06 APR 2022 | 1 LMI NAME THERMAL PERFORMANCE OF COOLING TOWERS AT NTPC SIMHADRI | 006 REV: 06 | 3 REFERENCE DOCUMENT OGN | REV:05 APR:2021 | NAME: JHIMLI DHAR | NAME: I LAXMA REDDY | NAME: GIRISH CHANDRA CHOUKSE | 2 ¦ PA G E | SL NO CONTENT PAGE NO | 1 INTRODUCTION 4 | 2 OBJECTIVE 4 | 3 SUPERSEDED DOCUMENT 4 | 4 RECORDS OF REVISION 4 | 5 CW SYSTEM IN SIMHADRI 4 | 6 ROLE OF COOLING TOWERS IN POWER STATION 4 | 7 SALIENT TERMS USED IN CT TESTING 5 | 8 TEST PROCEDURE 5 | 9 PERFORMANCE OF COOLING TOWER 7 | 10 EVALUATION OF COOLING TOWER PERFORMANCE 8 | 11 FREQUENCY 9 | 12 COOLING TOWER REPORT FORMAT 9 | 13 REVIEW 10 | 3 ¦ PAGE | COOLING WATER SYSTEM PLAYS A VITAL ROLE IN DISSIPATION OF WASTE HEAT IN POWER STATION. MORE | THAN 60 % OF TOTAL HEAT INPUT TO THE PLANT IS FINALLY DISSIPATED AS WASTE HEAT. THE WASTE HEAT | FROM THE POWER PLANT IS CARRIES AWAY BY CIRCULATING WATER AND ULTIMATELY GETS DISSIPATED IN | COOLING TOWER. | 2.0 OBJECTIVE | THE PURPOSE OF THIS TEST IS TO DESCRIBE PROCEDURE FOR TESTING AND PERFORMANCE EVALUATION OF | THIS SUPERSEDES LMI | 006: THERMAL PERFORMANCE OF COOLING TOWERS AT | IN REVISION 5 ISSUED IN APR: 2021. | 4.0 RECORDS OF REVISION | ENTIRE LMI HAS BEEN REVISED ACCORDING TO THE EXTERNAL AUDIT EXCEPTION POINTS. | 5.0 CW SYSTEM | CW SYSTEM AT NTPC SIMHADRI IS CLOSED RECIRCULATING TYPE AND HAVING NATURAL DRAUGHT | NDCT | COOLING TOWERS NDCT. | FOUR NATURAL DRAFT COOLING TOWERS HAVE BEEN INSTALLED FOR 4 X 500 MW UNITS OF NTPC | SIMHADRI WHICH ARE OF COUNTERFLOW TYPE WITH SPLASH FILLS. | 6.0 ROLE OF COOLING TOWER IN POWER STATIONS | COOLING TOWERS PLAY AN IMPORTANT ROLE IN ENSURING THE THERMAL EFFICIENCY OF A GENERATING | STATION. THERMAL EFFICIENCY OF A STEAM TURBINE IS DEPENDENT ON THE TEMPERATURE OF THE | EXHAUST STEAM FROM THE LP TURBINE INTO THE CONDENSER. HEAT FROM THE STEAM SIDE OF THE | CONDENSER IS TRANSFERRED TO THE CIRCULATING WATER. THIS HEAT IS IN TURN TRANSFERRED TO THE | ATMOSPHERE IN COOLING TOWER. | IN CASE THE COOLING TOWER DOES NOT PERFORM SATISFACTORILY | THE COLDWATER TEMPERATURE OF THE | COOLING WATER WOULD GO UP. THIS IN TURN WOULD AFFECT THE CONDENSING TEMPERATURE OF STEAM | AND BACK PRESSURE IN THE CONDENSER. THIS WOULD RESULT IN AN INCREASED HEAT RATE AND | SUBSEQUENT INCREASE IN FUEL INPUT. | 7.0 SALIENT TERMS USED IN CT TESTING: | 7.1 APPROACH: | DIFFERENCE BETWEEN THE COLDWATER TEMPERATURE AT CT OUTLET AND INLET AIR WETBULB | TEMPERATURE. | 7.2 RANGE: | INLET TO CT | DIFFERENCE BETWEEN THE HOT WATER TEMPERATURE INLET TO CT AND COLDWATER TEMPERATURE | OUTLET OF CT | 7.3 TOWER CAPABILITY: | THE MOST RELIABLE MEANS TO ASSESS THE COOLING TOWER THERMAL PERFORMANCE IS TOWER CAPABILITY. | IT IS DEFINED AS THE PERCENTAGE OF WATER THAT THE TOWER CAN COOL TO THE DESIGN COLD WATER | COOLING RANGE | TEMPERATURE WHEN THE INLET WETBULB | WATER FLOW RATE IS ALL AT THEIR DESIGN | VALUE. | 7.4 EFFECTIVENESS: | RANGE * 100 | EFFECTIVENESS = | RANGE + APPROACH | RANGE = HOT WATER TEMP COLD WATER TEMP | APPROACH = COLD WATER TEMP WET BULB TEMP | 8.0 TEST PROCEDURE: | 8.1 PARAMETERS TO BE MEASURED: | A CIRCULATING WATER FLOW: | THE WATER FLOW CAN BE MEASURED BY MEASURING THE CW PUMP AND EVALUATING THE FLOW | FROM THE PUMP CHARACTERISTIC CURVES OR BY PITOT TUBE. THE FLOW MEASUREMENT CAN BE DONE IN | THE PIPE AT PITOT TUBE PIT WHICH IS SUFFICIENT FOR TRAVERSING UP TO THE CENTER OF 3.2METER ER. | REFER TO PG TEST PROCEDURES FOR MET OF CALCULATIONS. | B HOT WATER TEMPERATURE MEASUREMENT: | THE THERMOMETERS MAY BE INSERTED INTO THE CHANNEL WHERE WATER DISTRIBUTION NETWORK IS | OPEN OR INTO THE THERMO WELLS PROVIDED ON THE INLET RISER. | 11:32:33 | 454565 IDATE:05 | 202311:32:33 | WRT THE REVISED TC DOCUMENT NO: COSISO00OGN | 002 REV 02 AUG. 2023 | THE LOCATION | MANAGEMENT INSTRUCTION LMI OF PERFORMANCE TESTING OF CONDENSER AIR EXTRACTION PLANT I.E | 002 REVISION IS DONE. | 454565 | 002 REV 03 AUG | 23 MAY PLS. BE APPROVED. | SMNSTPS | 11:47:07 | 09:48:01 | 10:29:22 | NO CHANGE IS SUGGESTED. | 12:19:33 | 12:29:47 | 13:10:17 | 09:28:21 | PERFORMANCE TESTING OF CONDENSER AIR | EXTRACTION PLANT | REV: 03 AUGUST 2023 | TITLE PERFORMANCE TESTING OF CONDENSER AIR EXTRACTION PLANT | 002 REV:03 AUGUST 2023 | 1 LMI NAME PERFORMANCE TESTING OF CONDENSER AIR EXTRACTION PLANT | 002 REV: 03 | REV:02 AUGUST:2023 | REV:02 APR 2022 | 2 ¦ PAGE | 2 SUPERSEDED DOCUMENTS | 3 RECORDS OF REVISION | 4 SCOPE | 5 PROCEDURE | 6 CALCULATIONS | 7 REVIEW | 8 ANNEXURE | THE CONDENSER AIR EXTRACTION PLANT IS PROVIDED TO RAPIDLY EVACUATE AIR AND ANY OTHER NON | FROM THE CONDENSER STEAM SPACE AND | CONDENSABLE GASES DURING HOGGING | ASSOCIATED PIPEWORK ON START UP | WITH THE MACHINE ON LOAD. | THE PLANT DESIGN AT NTPC SIMHADRI SUPER THERMAL POWER STATION IS HAVING VACUUM PUMPS OF LIQUID | RING TYPE. | INTERNAL | THE PERFORMANCE OF THE AIR EXTRACTION SYSTEM CAN BE AFFECTED BY SECONDARY COOLER FOULING | PLANT LEAKAGES | THE PERFORMANCE OF THIS TYPE OF PLANT VARIES THROUGH OUT THE YEAR AS DOES THAT OF | IN ADDITION | CONDENSER WITH THE CHANGE IS CW INLET TEMPERATURE FROM WHICH SUB SYSTEM COOLING WATER IS | AIR RATIO TO BE HANDLED BY | DRAWN. THIS WILL ALSO AFFECT THE SUCTION CONDITIONS | VARYING THE WATER VAPOR | THE PLANT. | CAUSED BY AIR BLANKETING | MAY BE DUE TO LEAKAGE WELL IN THE EXCESS OF AIR | POOR CONDENSER VACUUM | EXTRACTION PLANT CAPACITY OR A DIRECT SHORTFALL IN THE PERFORMANCE OF THE AIR EXTRACTION PLANT. THIS | A SIMPLE TEST TO DETERMINE THE | RESULTS FROM THE GENERAL DIFFICULTY IN IDENTIFYING CONDENSER AIR LEAKS | AIR EXTRACTION PLANT PERFORMANCE IS THEREFORE ESSENTIAL TO IDENTIFY THE PRIMARY CAUSE OF ANY PROBLEM. | 2.0 SUPERSEDED DOCUMENTS: | 002 REV:02 | APR 2022 | 3.0 RECORDS OF REVISION: | THE REVISION IS DONE DUE TO THE TC DOCUMENT REVISION. | 4.0 SCOPE: | THE SCOPE OF TESTING EXTENDS TO VACUUM PUMPS USED FOR AIR EXTRACTION OF SIMHADRI STATION. | 5.0 PROCEDURES: | THE PROCEDURE FOR MEASUREMENT OF THE PERFORMANCE OF POWER STATION CONDENSER AIR | EXTRACTION PLANT IN RESPECT OF ITS AIR HANDLING CAPACITY IS AS FOLLOWS: | PLANT TESTING CONDITIONS: | I UNIT SHOULD BE AT FULL LOAD IN NORMAL STABLE CONDITION. | TEMPERATURE | PRESSURE SHOULD BE NORMAL RANGE. | II VACUUM PUMP SEAL WATER FLOW | 4 ¦ P A GE | 5.1.1 RECORD ALL THE PARAMETERS AS PER ANNEXURE I WHEN SINGLE PUMP IS RUNNING | I CHANGEOVER OF RUNNING PUMP WITH STAND BY PUMP AND RECORD ALL PARAMETERS AS PER | ANNEXUREI. | II COMPARE CONDENSER BACK PRESSURE AFTER CORRECTION FOR LOAD AND CW INLET TEMPERATURE | WHEN TWO PUMPS ARE RUNNING SEPARATELY. | REMARKS: CORRECTED CONDENSER BACK PRESSURE SHOULD BE SAME FOR BOTH VACUUM PUMPS. | OTHERWISE | HIGHER BACK PRESSURE WITH ANY PUMP IN SERVICE INDICATES POOR PERFORMANCE OF | THE PUMP. | 5.2.1 RECORD ALL PARAMETERS AS PER ANNEXUREI WHEN ANY ONE PUMP IS RUNNING | I START STAND BY VACUUM PUMP AND RECORD ALL PARAMETERS AS PER ANNEXUREI | II OBSERVE DEVIATION IN CONDENSER BACK PRESSURE AFTER CORRECTING FOR LOAD AND CW INLET | TEMP. | INGRESS IN CONDENSER IS MORE THAN THE CAPACITY OF A SINGLE PUMP. | 6.0 CALCULATION: | I DERIVE SATURATION TEMPERATURE CORRESPONDING VACUUM PUMP INLET PRESSURE. VACUUM | PUMP OPERATING WATER TEMPERATURE SHOULD LESS THAN SATURATION TEMPERATURE | II DIFFERENCE BETWEEN SEALING WATER | COOLING WATER TEMPERATURE SHOULD BE | THEN HEAT EXCHANGER | APPROXIMATELY 2.5 DEGREE C MAX. IF THE TEMPERATURE IS MORE | III TRENDING OF ROTAMETER READING TO BE DONE FOR EARLY INTERVENTION OF AIR INGRESS. | IV HELIUM LEAK TEST IS TO BE CONDUCTED FOR IDENTIFICATION AND RECTIFICATION OF AIR INGRESS | POINTS. AFTER ATTENDING THE DEFECTS CONDENSER BACK PRESSURE IMPROVEMENTS TO BE | RECORDED. …………… TMD | 5 ¦ P A GE | 7.0 REVIEW: | THE OF PROJECT IS RESPONSIBLE FOR REVIEWING THIS LMI ON TWO YEARLY BASIS OR AS OR | NECESSARY. | ANNEXUREI | VACUUM LIQUID RING PUMP LOG SHEET ROUTINE CHECK LIST | LIQUID RING | ROUTINE CHECK LIST | SL NO PARAMETER UNIT RUNNING | PARAMETER | 1 UNIT LOAD MW | 3 VACUUM PUMP SEALING WATER TEMP. DEG. C | DEG. C | TEMPERATURE OF KSC | 4 COOLING WATER INLET PRESSURE | HEAT EXCHANGER | WORKING FLUID | 5 COOLING WATER WORKING FLUID OUTLET PRESSURE KSC | TEMPERATURE TEMP OF HEAT EXCHANGER | SEALING WATER | 6 STRAINER SEALING WATER DP | 7 SEPARATOR LEVEL | 8 SEPARATOR AIR FLOW ROTAMETER READING KG | ROTAMETER READING | 9 RECIRCULATION PUMP FLOW M3 | 10 VACUUM PUMP MOTOR CURRENT A | 11 DIRECTION OF ROTATION OF MOTOR VIEWED FROM MOTOR | NDE SIDE. | 12 INSTRUMENT AIR PRESSURE KSC. | MANUAL | 13 FEED WATER FLOW VALVE OF SEPARATOR TANK STATUS. AUTO | 14 NO. VACUUM PUMPS RUNNING | 6 ¦ P A GE | PAGE 1 OF 5 | 202510:29:28 | 10:29:28 | 192109 IDATE:03 | LMI 252 | SUBJECT:REVISION OF LMI FOR DETERMINATION OF SPECIFIC WATER COONSUMPTION | LMI IS REVISED ON THE BASIS OF COSISO00OIN | 034 REV :03 APRIL 2025. | SUBMITTED FOR APPORVAL | 192109 | PAGE 2 OF 5 | LMI HANS BEEN REVISED AS PER THE REVISED OIN. | LMI IS IN LINE WITH THE OIN. MAY PLEASE BE APPROVED. | 10:36:28 | 19:35:16 | PAGE 3 OF 5 | 15:20:59 | अजय िगिर अपर महाप्रबंधक | AJAY GIRI 007629 ADDL. GENERAL MANAGER | AJAYGIRI@NTPC.CO.IN | 7440228332 | 15:35:57 | PAGE 4 OF 5 | 21:19:16 | 19:42:57 | PAGE 5 OF 5 | 11:29:59 | 17:19:08 | 18:45:52 | [TYPE HERE] | DETERMINATION OF SPECIFIC WATER CONSUMPTION | 034 REV:04 | 1 LMI NAME DETERMINATION OF SPECIFIC WATER CONSUMPTION | REV:03 | APRIL:2025 | 034 REV:03 APRIL 22 | 4.0 OBJECTIVES 2 | 5.0 METOLOGY 3 | 6.0 REVIEW 4 | 7.0 CHECK LIST 56 | 8.0 ANNEXURE 78 | TITLE DETERMINATION OF SPECIFIC WATER CONSUMPTION | LARGE QUANTITY OF WATER IS USED IN THERMAL POWER STATIONS FOR COOLING IN CONDENSERS | OF STEAM TURBINE. IT IS EITHER USED IN ONCE THROUGH MODE OR IN CLOSE CYCLE MODE. IN | WHATEVER WATER IS TAKEN FROM WATER BODY IS GIVEN BACK TO | ONCE THROUGH MODE | WATER BODY | EXCEPTING LITTLE QUANTITY CONSUMED IN EVAPORATION. IN CLOSE CYCLE MODE | HEAT PICKED UP IN CONDENSER IS EVACUATED TO ATMOSPHERE THROUGH COOLING TOWERS. IN | CONTINUOUS ADDITION OF MAKEUP WATER IS REQUIRED TO TAKE CARE OF THE | SUCH CASES | EVAPORATION AS WELL AS DRIFT LOSSES OCCURRING IN COOLING TOWERS. ALSO | A PART OF RE | CIRCULATING WATER IS REPLENISHED WITH MAKEUP WATER TO MAINTAIN THE SALT LEVEL TO | ACCEPTABLE LIMITS. | IN ADDITION TO CONSUMPTION IN CW | CT CIRCUIT | LARGE QUANTITY OF WATER IS CONSUMED | IN PRODUCTION OF DEMINERALIZED WATER | AS MAKEUP IN THE | FOR WET DISPOSAL OF ASH | COOLING CIRCUIT OF VARIOUS COOLERS LIKE LUB OIL COOLERS | GENERATOR COOLERS | COMPRESSORS | IN HOUSEKEEPING AND FIREFIGHTING APPLICATIONS. WATER IS ALSO CONSUMED FOR | OFFICES AND FOR DOMESTIC APPLICATION IN TOWNSHIP ETC. | WATER BEING A SCARCE RESOURCE ALL EFFORTS ARE TO BE MADE TO MINIMIZE THE | CONSUMPTION OF WATER. THIS OBJECTIVE IS ACHIEVED THROUGH PROPER SELECTION AND | SYSTEMS AT INITIAL STAGE ITSELF AND BY FOLLOWING | DESIGN OF POWER PLANT SCHEMES | HELPS IN IDENTIFYING THE WASTAGE | INEFFICIENT UTILIZATION OF WATER. SUCH AUDITS | COMPARE THE PRESENT FLOWS IN DIFFERENT WATER CIRCUITS AND COMPARE IT WITH THE | SYSTEMS. ALL | DESIGNED FLOWS | AUDIT AND TRY TO BRING THEIR WATER CONSUMPTION WITHIN THE NORMS SPECIFIED AS PER | PROTECTION | ENVIRONMENT PROTECTION AMENDMENT RULES 2015. | AS A FIRST STEP TOWARDS SYSTEMATIC EFFORTS FOR MINIMIZATION OF WATER CONSUMPTION | IS ESSENTIAL TO PERIODICALLY MEASURE | ASSES TOTAL WATER CONSUMPTION AND SPECIFIC | WATER CONSUMPTION OF THE STATION. REGULAR MONITORING AND TRENDING OF THESE | PARAMETERS WILL HELP IN QUICK IDENTIFICATION OF ANY DETERIORATION. IT WILL ALSO HELP IN | ASSESSMENT OF IMPACT OF ANY MODIFICATION | MEASURES TAKEN FOR WATER CONSERVATION. | SIMHADRI TWO TYPES OF WATER BEING USED: | SEA WATER: FOR CONDENSER COOLING AND ASH DISPOSAL. THIS SEA WATER IS DRAWN FROM | BAY OF BENGAL THROUGH 3 NO OF SEA WATER PUMPS. THE HOT WATER FROM CONDENSER IS | COOLED IN NDCTS AND PART OF IT IS USED FOR ASH DISPOSAL AND THE REMAINING WATER IS SENT | BACK TO SEA THROUGH EDP EFFLUENT DISPOSAL PUMPS | EFFLUENT DISPOSAL PUMPS | SWEET WATER: FOR PROCESS REQUIREMENT AND POTABLE PURPOSE. SWEET WATER IS DRAWN FROM | YELERU CANAL AND IS PUMPED TO RESERVOIR THROUGH SWEET WATER PUMPS. FROM RESERVOIR | REQUIRED WATER IS DRAWN AND IS PROCESSED IN PT PLANT. THIS PROCESSED | WATER IS SUPPLIED AS DM WATER | CLARIFIER WATER AND POTABLE WATER. | APR:2022 | FOLLOWING NEW POINTS ARE ADDED | 1. CLAUSE NO. 4.4 AND 4.5 ADDED | 2. CLAUSE NO. 5.7 | 5.8 AND 5. 9 ADDED. | 4.0 OBJECTIVES | 4.1 FOR SIMHADRI CONSENT QUANTITIES ARE: | MILLION LITRES PER DAY | SWEET WATER ................................21.6 MLD MILLION LITRES PER DAY | SEA WATER………………………….429.24 MLD | 4.2 THIS LMI WILL HELP TO MONITOR THE SPECIFIC WATER CONSUMPTION AND MAINTAIN WATER | CONSUMPTION WITHIN CONSENT LIMITS. | FROM NATURAL RESOURCE | 4.3 DETERMINATION OF SPECIFIC WATER CONSUMPTION ON WITHDRAWAL FROM NATURAL RESOURCE | BASIS OF THE STATION IS TO BE DONE ON MONTHLY | CUMULATIVE | QUARTERLY | AND YEARLY CUMULATIVE BASIS. | 4.4 DETERMINATION OF SPECIFIC WATER ON INDUSTRIAL CONSUMPTION BASIS OF THE STATION IS TO BE | DONE ON MONTHLY | QUARTERLY AND YEARLY CUMULATIVE BASIS. | 90042 IDATE:11 | 09:43:44 | 202209:43:44 | THE LOCATION MANAGEMENT INSTRUCTION LMI OF "SYSTEM FOR AUDIT OF LOCATION | MANAGEMENT INSTRUCTIONS LMIS OF POWER STATION" I.E LMI | 003 REV : 03 MAY 2022 | 003. | ENTIRE LMI IS REVISED IN LINE WITH CC OS REVISION NO 3 APRIL 2022COSISO00OGN | COS-ISO-00-OGN | 5.8.2. NEW CLAUSE | 5.1.3 | 5.1.4 HAVE BEEN ADDED. | 5.1.2 | ISSUE RAISED DURING LAST EXTERNAL AUDIT IS ALSO COMPLIED. | REVIEW OF THIS LMI IS DONE AS PER SECHEDULE. | 90042 | LMI CHNECKED AND FOUND OK. | 10:10:18 | FORWARDED FOR APPROVAL OF CA | REVIEWEND AND FOUND OK | 17:58:41 | 20:47:38 | 11:00:47 | SYSTEM FOR AUDIT OF LOCATION MANAGEMENT | INSTRUCTIONS LMIS OF POWER STATION | NTPC NTPC SIMHADRI | TITLE SYSTEM FOR AUDIT OF LOCATION MANAGEMENT INSTRUCTIONS | LMIS OF POWER STATION | 1 LMI NAME SYSTEM FOR AUDIT OF LOCATION MANAGEMENT | 003 REV : 03 MAY | 2022 | COSTCOGN | 3 REFERENCE EOC | 34323 DATE 22.04.2022 | 4 SUPERSEDED LMI | 003 ISSUE NO 1 REV. NO. 02 DATE: | DOCUMENT DECEMBER 2019 | 5 PREPARED BY NAME: SUBIR DEBNATH | 6 CHECKED BY NAME: JHIMLI DHAR | 7 REVIEWED BY NAME: I LAXMA REDDY | 8 APPROVED BY NAME: GIRISH CHANDRA CHOUKSE | SL NO PARTICULARS PAGE NO | INTRODUCTION 4 | 3.0 SUPERSEDED DOCUMENTS 4 | 4.0 RECORD OF REVISION 5 | 5.0 PROCESS 5 | 5.1 RESPONSIBILITIES 5 | 5.2 INTERNAL TECHNICAL COMPLIANCE AUDIT OF LMIS BY POWER 6 | STATION | 5.3 EXTERNAL TECHNICAL COMPLIANCE AUDIT OF LMIS BY REGIONAL 6 | 5.4 THIRD PARTY AUDIT 7 | 5.5 PRE AUDIT PREPARATIONS 7 | 5.6 GUIDELINES FOR CONDUCTING THE AUDIT 8 | 5.7 PREPARATION OF AUDIT REPORT AND ACTION PLAN 10 | 5.8 POST AUDIT ACTIVITIES AND FOLLOW UP 11 | 5.9 A FLOW DIAGRAM GIVING THE ACTIVITIES OF TC AUDIT IS GIVEN IN 12 | ANNEXURE – 2 | 5.10 RECORDS 12 | 6.0 ASSOCIATED DOCUMENTS 12 | 7.0 REVIEW 12 | ANNEXURE 1 SUGGESTED PLANT AREAS FOR TECHNICAL COMPLIANCE AUDIT. 13 | ANNEXURE 2 A FLOW DIAGRAM GIVING THE ACTIVITIES OF TC AUDIT. 17 | ANNEXURE –3 FORMAT FOR REPORT OF TECHNICAL COMPLIANCE AUDIT OF 18 | LMIS. | ANNEXURE –4 FORMAT FOR REPORTING FINDINGS OF TC AUDIT. 19 | SYSTEM FOR AUDIT OF LOCATION MANAGEMENT INSTRUCTIONS LMIS OF | POWER STATION | INTRODUCTION | THIRD | THE SYSTEM COVERS THE TECHNICAL COMPLIANCE AUDIT INTERNAL | EXTERNAL | PARTY OF LOCATION MANAGEMENT INSTRUCTIONS OF POWER STATIONS SO THAT THE OF | THE STATION IF FULLY AWARE OF THE STATUS OF THE IMPLEMENTATION OF THE LMI AND TAKE | CORRECTIVE ACTIONS IN CASE OF DEVIATIONS. THIS WILL HELP THE STATION TO SATISFY | TECHNICAL AUDIT TEAM CONSTITUTED BY CORPORATE OS. THE OBJECTIVE OF THE | TECHNICAL COMPLIANCE AUDIT OF LMI OF POWER STATION ARE AS FOLLOWS : |  TO ENSURE THAT POWER STATION HAS PREPARED THE LOCATION MANAGEMENT | DIRECTIVESODS | INFORMATION NOTESOINS] AND ISSUED FOR IMPLEMENTATION TO ALL | CONCERNED. |  TO ENSURE THAT LMIS PREPARED ARE IN LINE WITH STATUTORY STANDARDS AND | REQUIREMENTS | FIND OUT DEVIATION |  TO ENSURE COMPLIANCE OF LMIS IN THE POWER STATION | AND ARRANGE TIME BOUND PREVENTIVE AND CORRECTIVE ACTION PLAN. | AMENDMENT AND ARRANGE |  TO IDENTIFY AREAS WHERE THE LMIS NEED UPDATION | TIME BOUND ACTION PLAN FOR THEIR MODIFICATIONS. |  TO ENABLE THE POWER STATIONS TO COMPLY TECHNICAL AUDIT TEAM CONSTITUTED | BY CORPORATE OS. |  TO ASSIST POWER STATION MANAGEMENT IN DEMONSTRATING TO EXTERNAL | AGENCIES THAT THE POWER STATION HAS IN PLACE SOUND TECHNICAL SYSTEM FOR | 2.0 SCOPE | AUDIT OF LMI’S OF SIMHADRI SUPER THERMAL POWER STATION | 3.0 SUPERSEDE DOCUMENTS | DECEMBER2019 | ENTIRE LMI IS REVISED IN LINE WITH CC OS REVISION NO 3 APRIL 2022COS | ISO00OGN | 5.8.2 | MINOR CHANGES HAVE BEEN DONE IN ANNEXURE 2. | NEW CLAUSE 5.1.2 | 5.1.4 HAVE BEEN ADDED | 5.1 RESPONSIBILITIES | 5.1.1 THE OF O | M OF THE POWER STATION IS THE NODAL POINT FOR THE | LMIS IMPLEMENTATION. THE TECHNICAL COMPLIANCE AUDIT OF LMI’S IS | AN IMPORTANT TOOL FOR REVIEWING LMIS STATUS. | AND THEIR | ENSURE TIMELY PREPARATION AND IMPLEMENTATION OF LMIS | OIN IS | STATION SHALL ENSURE THAT ALL RELEVANT CONTENT OF OD | CAPTURED IN LMIS. | LMIS IS CHECKED THROUGH AUDITS AS ENVISAGED IN THE SYSTEM. | 5.1.5 THERE WILL BE TWO TECHNICAL COMPLIANCE AUDITS OF LMIS IN EACH | FINANCIAL YEAR AS UNDER: | I INTERNAL AUDIT: THE STATION WILL CONDUCT THE FIRST AUDIT INTERNALLY BY THE | END OF FIRST SIX MONTHS I.E. BY SEPTEMBER EVERY YEAR | TO BE COORDINATED BY | II EXTERNAL AUDIT: THE SECOND AUDIT WOULD BE EXTERNAL AUDIT WITH THE HELP | OF OTHER POWER STATIONS IN THE REGION BY THE END OF NEXT SIX MONTHS I.E. BY | MARCH EVERY YEAR AND WILL BE COORDINATED BY REGIONAL QUARTER OS. | 5.1.6 THERE SHALL ALSO BE A THIRDPARTY AUDIT WITH AUDITORS WHO ARE EXTERNAL | TO NTPC OF LMI IMPLEMENTATION AT STATIONS. THE FREQUENCY OF THE | AUDIT WILL BE ONCE A YEAR | AND ONCE IN TWO YEARS | FOR STATIONS WHERE TWO YEARS HAVE ELAPSED AFTER | PARTY AUDIT WILL BE DECIDED BY CONCERNED STATION | RHQ. | 5.2 INTERNAL TECHNICAL COMPLIANCE AUDIT OF LMIS BY POWER STATION | 5.2.1 THE INTERNAL TCALMI WOULD BE DONE BY THE MONTH OF SEPTEMBER | 5.2.2 THE INTERNAL AUDIT TEAM WOULD BE AT LEAST A THREE 3 MEMBER TEAM – | AND ADDITIONAL MEMBERS AS PER REQUIREMENT. THE LEVEL WOULD BE | SR MANAGER | AGM. | DGM | THE PROPOSAL GIVING THE NAMES OF THE AUDIT TEAM WOULD BE INITIATED | AUGUST EVERY YEAR ALONG WITH THE NAMES OF ONE ENGINEER EACH FROM | CONCERNED DISCIPLINES WHO WOULD WORK AS COORDINATOR FOR THAT | DISCIPLINE NAME TO BE FINALIZED IN CONSULTATION WITH OF O | NAME TO BE FINALIZED IN CONSULTATION WITH HEAD OF O | THE PROPOSAL WOULD ALSO INCLUDE THE DATES OF AUDIT AND ITS SCHEDULE. | ONE MEMBER OF THE TEAM WOULD BE NOMINATED AS TEAM LEADER. THE | IT WOULD BE CIRCULATED TO ALL CONCERNED S. | 5.2.3 THE AUDIT TEAM CAN COOPT ANY OTHER PROFESSIONAL OF THE POWER | STATION AS PER REQUIREMENT | WITH THE APPROVAL OF CONCERNED . | 5.3 EXTERNAL TECHNICAL COMPLIANCE AUDIT OF LMIS BY REGIONAL OS. | 5.3.1 THE EXTERNAL TCALMI WOULD BE DONE BY THE MONTH OF MARCH EVERY | YEAR. THIS WOULD BE COORDINATED BY OF OS IN REGION. | 5.3.2 THE AUDIT TEAM WOULD BE AT LEAST A THREE 3 MEMBER TEAM – ONE | ADDITIONAL MEMBERS AS PER REQUIREMENT. THE LEVEL WOULD BE MANAGER | SR MGR | AGM. THE MEMBERS WOULD BE DRAWN FROM THE | REGION AND POWER STATIONS IN THE REGION OTHER THAN THE POWER STATION | WE AUDIT IS BEING CARRIED OUT. THE PROPOSAL GIVING THE NAMES OF | THE AUDIT TEAM WOULD BE INITIATED BY OF OS IN REGION BY THE | MONTH OF FEBRUARY EVERY YEAR AND PUT UP TO ED OF REGION FOR APPROVAL. | WHICH WOULD | THIS WOULD INCLUDE THE DATES OF AUDIT AND ITS SCHEDULE | M OF POWER STATION. ONE | BE FINALISED IN CONSULTATION WITH OF O | MEMBER OF THE TEAM WOULD BE NOMINATED AS TEAM LEADER. AFTER | THIS WOULD BE SENT TO THE OF POWER STATION | FINALIZE THE NAMES OF LOCAL COORDINATORS OF VARIOUS DISCIPLINES IN THE | POWER STATION TO FACILITATE THE AUDIT. | 5.4 THIRD PARTY AUDIT | THE THIRD PARTY AUDIT OF LMIS WOULD BE DONE AS PER THE FREQUENCY | OF CONDUCTANCE OF THIRD PARTY AUDIT WILL BE ENSURED BY OF OS OF | CONCERNED REGION. | 5.5 PRE AUDIT PREPARATIONS | 5.5.1 THE DATES OF TCALMI INTERNAL OR EXTERNAL AUDITS WOULD BE FIXED IN | SUCH A WAY THAT THERE WOULD BE GAP OF AT LEAST 15 DAYS BETWEEN THIS | AUDIT AND THE TECHNICAL AUDIT OF THE POWER STATION DONE BY | CORPORATE OS. | 5.5.2 THE TEAM LEADER OF EXTERNAL AUDIT WILL CONFIRM AT LEAST ONE WEEK IN | AS PER THE AUDIT SCHEDULE FINALISED BY THE | CARRYING OUT THE AUDIT | REGIONAL QUARTER. | 202316:50:01 | 528517 DATE: 29 | 16:50:01 | SHAFT VOLTAGE AND CURRENTS IN LARGE TURBO GENERATORS | 014 | 014 HAS BEEN REVISED BY COS IN APRIL 2022. NO CHANGES ENVISAGED BY COS. | LMI IS REVIEWED. | A FREQUENCY OF SHAFT VOLTAGE MEASUREMENT CHANGED FROM MONTHLY TO QUARTERLY. | B GENERATOR VOLTAGE AND POWER FACTOR READING ADDED IN CHECKLIST ANNEXUREI. | REV 3 | ISSUE3 | MAY 2020 | SUBMITTED BY : | ELECT MAINT SKVERMA03@NTPC.CO.IN | 10:03:00 | 528517 | REVIEWEND AND NECESSARY CHANGES DONE. | REVISION NUMBER UPDATED. | 11:11:32 | 18:43:26 | CHECK LIST ENCLOSED. | LMI REVNIEWED AND REVISED OCT23 | 19:55:26 | 10:00:33 | 11:03:16 | REVISEDN LMI MAY PLEASE BE ACCORDED APPROVAL. | 12:59:26 | 08:48:51 | 09:28:23 | ISSUE: 3 | REVISION: 3 | REVISION 3 | ISSUE NO.: 3 | SHAFT VOLTAGES AND CURRENT IN LARGE | TURBO GENERATORS | NTPC LIMINTED. | LMINAME : SHAFT VOLTAGES AND CURRENT IN LARGE | ISSUE NO. 3 REVISION : 3 DATE :OCT 2023 | PREPARED BY SUMIT KUMAR VERMA SR. MANAGER EM | CHECKED BY MATHEW EIPE KOVOOR GM MAINT | SHAFT VOLTAGES AND CURRENTS IN LARGE TURBO GENERATOR | 1.1 CROSS MAGNETIZATION OF THE TURBINE 4 | 1.2 GENERATOR SHAFT VOLTAGE 4 | 1.3 STATIC CHARGES DEVELOPED ON THE TURBINE BLADES 4 | 2.0 SCOPE 5 | 3.0 REFERENCE DOCUMENT 5 | 4.0 SUPERSEDED DOCUMENTS 5 | 5.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED 5 | 6.0 SHAFT GROUNDING PROCEDURE 5 | 7.0 METOLGY OF IMPLEMENTATION 6 | 8.0 FREQUENCY OF CHECKING AND MEASUREMENTS 6 | 10.0 THE EXCEPTION REPORTING | DISPENSATION OF 7 | 11.0 RECORD KEEPING 7 | 12.0 REVIEW 7 | 13.0 RECORDS OF REVISION 7 | 14.0 ANNEXURE1 7 | WHICH CAN CAUSE DAMAGES TO THE BEARINGS AND GOVERNOR | THE FLOW OF CURRENT | CAN OCCUR DUE TO FOLLOWING | GEAR | FROM THE TURBINE GENERATOR SHAFT TO GROUND | REASONS. | 1.1 CROSS MAGNETIZATION OF THE TURBINE: | WHILE ROTATING CAN DEVELOP A | THE RESIDUAL MAGNETIZATION OF THE TURBINE SHAFT | VOLTAGE ALONG ITS LENGTH. WHEN THE TURBINE SHAFT GETS TWO LOW RESISTANCE POINTS | TO THE EARTH POTENTIAL AND THE SHAFT VOLTAGE GETS SHORT CIRCUITED THROUGH THE | CURRENT MAY FLOW IN SUCH A DIRECTION | TURBINE HOUSING | AS TO INDUCE A SHAFT | VOLTAGE IN THE SAME DIRECTION | AS THE ORIGINAL VOLTAGE. | THIS IS A SELF EXCITATION CONDITION WHICH CAN CAUSE VERY HIGH CURRENTS AND CAUSE | SERIOUS DAMAGE TO THE TURBINE. THERE HAVE BEEN A FEW SUCH INCIDENCES OF | DAMAGE REPORTED ELSEWHERE. | GENERATOR SHAFT. TO PREVENT CIRCULATION OF CURRENT THROUGH THE BEARINGS | DRIVEN | OR THE BEARING PEDESTAL | BY THIS VOLTAGE EITHER ONE OR BOTH BEARINGS OR THE BEARING PEDESTAL ARE | INSULATED FROM GROUND. ALL THE OIL PIPE LINE | WHICH COME IN CONTACT WITH | OIL SEALS | GENERATOR SHAFT ARE ALSO INSULATED. IN THE CASE OF MACHINES WITH EXCITER | COUPLED | THE COUPLING IS ALSO NORMALLY INSULATED. IT IS DIFFICULT TO MEASURE THE | RESISTANCE OF THIS INSULATION AS THE SHAFT IS EFFECTIVELY EARTHED AT A NUMBER OF | LOCATIONS THROUGH THE TURBINE. | 1.3 STATIC CHARGE DEVELOPED ON THE TURBINE BLADES: | DUE TO THE FRICTIONAL FLOW OF STEAM AND DROPLETS OF WATER BEING THROWN OVER THE | TURBINE BLADES IN THE LAST STAGES A STATIC VOLTAGE IS PRODUCED | WHICH CAN BUILD UP | NTPC SIMHADRI 5 | TO HIGH VALUES AND RESULT IN DISCHARGES TO EARTH POTENTIAL | THROUGH THE BEARINGS | PUNCTURING THE OIL FILM. | THE GROUNDING IS PROVIDED BETWEEN LP TURBINE | FOR KWU TURBINE AT SIMHADRI | AND GENERATOR. | TO AVOID DAMAGES DUE TO THE ABOVE REASONS TO THE BEARING AND THE GOVERNING | THE SHAFT VOLTAGE MEASUREMENT IS DONE. | THIS LMI COVERS THE UNIT # 1 | 500MW WATER COOLED GENERATOR SHAFT | CURRENT. | VOLTAGES | 014. | MAY2022 | 4.0 SUPERSEDED DOCUMENTS: LMI | THE SHAFT GROUNDING BRUSHES WHICH OPERATE IN A TILE ENVIRONMENT AND DO NOT | ARE LIKELY TO BECOME POOR CONDUCTOR IN THE COURSE OF | CARRY CURRENT NORMALLY | REF 8.0 | TIME. PERIODIC CHECKING REF 8.0 | CLEANING OF THE AREA AND INSPECTION OF | BRUSHES HAS TO BE DONE TO AVOID THIS SITUATION. | THE SHAFT GROUNDING SHALL NOT BE MADE AT MORE THAN ONE LOCATION. | 6.0 SHAFT GROUNDING PROCEDURE: | OIL PIPE LINES | THE BEARINGS AT EITHER END OF THE GENERATOR TOGETHER WITH SEALS | ARE INSULATED. GENERATOR SHAFT GROUNDING IS ACHIEVED THROUGH 2 BRUSH HOLDERS | WITH 4 CARBON BRUSHES AT BEARING NO 5 . THE BRUSH HOLDERS AND EARTH LEADS SHALL | BE WELL INSULATED TO AVOID ALTERNATIVE GROUND PATHS. | NTPC SIMHADRI 6 | 7.0 METOLOGY OF IMPLEMENTATION: | TO ENSURE THE ROTOR GROUNDING ARRANGEMENT AT THE TURBINE END | THE SHAFT VOLTAGE | SHOULD ALSO BE MEASURED AT EXCITER END W.R.T TURBINE END. THE SHAFT VOLTAGE | MEASURED IN THIS WAY SHOULD THEN BE COMPARED WITH THE VOLTAGE MEASURED AT | EXCITER END W.R.T EARTH. | THE MONITORING OF SHAFT VOLTAGES IS THE SIMPLEST WAY OF DETERMINING WHETHER THE | BEARING INSULATION IS HEALTHY OR NOT. THE SHAFT VOLTAGE MEASUREMENT WILL BE | DONE WHEN THE MACHINE IS AT FULL LOAD. SIMILAR MACHINES IN A STATION COULD ALSO | FORM A BASIS FOR COMPARISON. LOW SHAFT VOLTAGE IN ANY MACHINE SHOULD BE | INVESTIGATED DURING AN OUTAGE TO CONFIRM WHETHER THE SAME IS INHERENT FOR THE | MACHINE. | THE CONTACT OF THE EARTHING BRUSHES WILL BE PERIODICALLY CHECKED REF 8.0. | COPPER LOADED | THE CARBON BRUSHES USED IN THIS APPLICATION ARE SPECIAL SILVER | GRAPHITE AND CARE SHOULD BE TAKEN TO ENSURE CORRECT REPLACEMENT. | 8.0 FREQUENCY OF CHECKING AND MEASUREMENTS: | SHAFT VOLTAGE MONITORING NEEDS TO BE CARRIED OUT ONCE IN EVERY MONTH AT FULL LOAD | FREQUENCY | GENERATOR ROTOR FIELD CURRENT AND EXCITATION FIELD | WITH REACTIVE POWER | CURRENT ANNEXURE1. | ANNEXURE-1 | THE SHAFT VOLTAGE MEASURED AT EXCITER END W.R.T TURBINE END NEEDS TO BE CARRIED | OUT QUARTERLY. ANNEXURE1 SL.NO. 1A. | ANNEXURE-1 SL.NO. 1A | WHEN SHAFT VOLTAGE FALLS BELOW 75% OF THE MINIMUM REFERENCE VALUE FOR THE | MACHINE | THE INSULATION SHOULD BE CHECKED AT THE EARLIEST OPPORTUNITY BY | MONITORING THE CARBON BRUSH HEALTHINESS AND CHECKING OF THE GROUND CONNECTION. | 108850 | EMLMIPTF | 10:51:22 | 202410:51:22 | 008 INSPECTION AND | PROTECTION OF WATER COOLED GENERATOR STATOR WINDBING | PTFE E CONNECTIONS. O | NO CHANGES WERE SUGGESTED BY COS. | PUT UP FOR PERIODICAL REVIEWING OF THE LMI. | NO CHANGES | PUT UP FNOR REVIEW PLZ NO CHANGES | 11:04:20 | 11:26:31 | 17:40:01 | PLEASE MNODIFY LMI AS STANDARD LMI FORMAT AS MENTIOND IN LMI | 09:20:58 | LMI MONDIFIED AS PER NEW FORMAT. | 12:18:00 | 11:35:17 | 16:31:51 | 16:42:37 | 23:01:28 | 23:10:17 | INSPECTION AND PROTECTION OF WATER | COOLEDGENERATOR STATOR WINDING PTFE | E CONNECTIONS | 008 REV:02 | MAY 2024 | 1 LMI NAME INSPECTION AND PROTECTION OF WATER | COOLED GENERATOR STATOR WINDING | PTFE E CONNECTIONS | MAY 22 | NAME: BALABALAJI AKULA | NAME:NAGESWARA RAO | NAME: DK TOMAR | A G M EMI | 8 REVIEWED BY NAME: S.J.DAVID | G M O | APPROVED BY NAME: S.K.SINHA | H O P SIMHADRI | TITLE INSPECTION AND PROTECTION OF WATER COOLED | GENERATOR STATOR WINDING PTFE E CONNECTIONS | 4.0 HYDRAULIC | LEAKAGE TEST 13 | DURING CAPITAL OVERHAULS | 5.0 FREQUENCY OF CHECKING | AND MEASUREMENTS | FOR IMPLEMENTATION | 7.0 EXCEPTION REPORTING AND | DISPENSATION OF DEVIATION | 8.0 REVIEW 4 | 9.0 CHECKLIST 5 | NUMBER OF | LARGE CAPACITY TURBO GENERATORS USING WATER COOLING | FAILURES OF PTFE ES HAVE BEEN RECORDED. OBJECTIVE OF THIS LMI IS | TO BRING OUT THE MODALITIES WITH REGARDS TO THE INSPECTION OF ES | HYDRAULIC TESTING OF PTFE ES DURING GENERATOR | OVERHAUL IN ORDER TO AVOID THE IN SERVICE FAILURE OF THESE ES AND | CONSEQUENT OUTAGE OF MACHINE. | LEAKAGE TEST DURING CAPITAL OVERHAULS | INSPECTION | TESTING TECHNIQUE ARE APPLICABLE WHILE THE | CARE | MACHINEHAS BEEN DISMANTLED AND ROTOR THREADED OUT DURING MAJOR | GENERATOR OVERHAUL. HYDRAULIC TESTING OF THE PRIMARY WATER SYSTEM | WILL BE DONE BY DRY NITROGEN AT 6 KG | CM2 PRESSURE FOR 48 HOURS AND | ANY LEAKAGE SHALL BE RECTIFIED BEFORE PUTTING THE GENERATOR BACK IN | SOMETIMES IT IS NECESSARY TO DO HELIUM GAS | DETECTOR TEST FOR DETECTION OF THE MINOR LEAKAGES. | DURING MAJOR OVERHAULING OF GENERATOR WHEN ROTOR HAS BEEN | THREADEDOUT FOLLOWING WOULD BE DONE: | D INSPECTION OF PTFE ES: | I. DAMAGE TO OUTSIDE SURFACE – WHERE MAJOR DAMAGE OR CUT LIKE | E HAS TO BE CHANGED. | THE PHYSICAL LOCATION | II. E ALIGNMENTAS FAR AS IS PRACTICABLE | OF THE ES SHOULD BE CHECKED FOR DISTORTION. CHECK FOR | DISTRIBUTION OF BARS WHERE ES CONNECTION TO WINDING ARE | FURTHER STRIPPING WILL NOT BE DONE | COVERED WITHINSULATION BOXES | UNLESS DAMAGE IS EVIDENT. MAJOR DISTORTION OR BADLY ALIGNED | IN CONSULTATION WITH THE | ES SHOULD BE CHANGED | MANUFACTURER. | III. CIRCUMFERENTIAL SPRING BACK RESISTANCE OF THE E IN NON | WITHRESPECT TO MOUNTING POSITION OF SCREWED FITTING. IN CASE OF | REBENDING OF THE ES IS | HIGHER SPRING BACK RESILIENCE | TEMPERATURE OF APPROXIMATELY 1500C WHICH CAN BE ATTAINED BY | INDUSTRIAL HOTBLOWER. | IV. CRIMPING CONNECTION INSPECT CRIMP CONNECTION FOR DOUBLE | WHEREVER NOT AVAILABLE IT IS TO BE CHANGED | CRIMPING | ACCORDINGLY. | V. A VISUAL INSPECTION OF ES SHOULD BE CARRIED OUT DURING MAJOR | OVERHAULS TO CHECK WHETHER ANY EXTERNAL CONTAMINATION OR | DEPOSITS HAVE BEEN FORMED. INTERNAL DEPOSITS COULD BE DUE TO | ACTIONS ARE TO BE TAKEN. TEFLON ES WITH INTERNAL DEPOSITS ARE | TO BE REMOVED AND A SAMPLE COLLECTED FOR FURTHER ANALYSIS. | E PROTECTION OF PTFE ES DURING GENERATOR | TO THE E DURING THE OPENING OF A GENERATOR AT THE TIME OF OVERHAUL. | F PROTECTION OF OPEN PIPES AND ES: THERE HAVE BEEN | INSTANCES WHERE BLOCKAGES HAVE BEEN FOUND IN PIPEWORK AND ES | 105535 IDATE:16 | 202217:08:13 | 17:08:13 | SUBJECT:LMI ON POLICY ON TECHNICAL MANAGEMENOT SYSTEM | SUBJECT: REVIEW OF LMI ON "POLICY ON TECHNICAL MANAGEMENT | SYSTEM"LMI | 001 ISSUE NO:01 REV:02 DATE :MAY 2022 | THERE ARE SOME CHANGES AS FOLLOWS: | STRUCTURE | DIVISIONS” | WITH “ OF PROJECT" | ISSUE RAISED REGARDING THIS LMI DURING EXTERNAL AUDIT IS ALSO COMPLIED. | THE REVIEW OF THIS LMI IS DONE AS PER SCHEDULE. | HOP SIMHADRI IS THE APPROVING AUTHORITY OF THE LMI. | SUBMITTED FOR KIND APPROVAL BY THE COMPETENT AUTHORITY. | 105535 | SUBMITNTED FOR APPROVAL OF COMPETENT AUTHORITY | 18:08:20 | FORWARDED FOR APPROVAL | REVIEWEND FOUND OK | 18:14:36 | 20:40:39 | 09:54:49 | ISSUE NO:01 REV:02 DATE MAY 2022 | POLICY ON TECHNICAL MANAGEMENT | TITLE POLICY ON TECHNICAL MANAGEMENT SYSTEM | 001 ISSUE NO:01 REV:02 | DATE: MAY 2022 | ENERGY EFFICIENCY AND MANAGEMENT GROUP | 1 LMI NAME POLICY ON TECHNICAL MANAGEMENT SYSTEM | 001 ISSUE NO:01 | REV:02 DATE :MAY 2022 | 3 REFERENCE COSISO00OD | 001 REV. NO.: 0 APRIL 2021 | REV :01 DEC 2019 | 8 REVIEWED BY NAME: R J JHA | DESIGNATION: GMO | 9 APPROVED BY NAME: GIRISH CHANDRA CHOUKSE | POLICY ON TECHNICAL MANAGEMENT SYSTEM | 3.0 SUPERSEDED DOCUMENTS 1 | 4.0 RECORD OF REVISION 1 | 5.0 STRUCTURE 2 | DIVISIONS | 5.2 POWER STATIONS 2 | 5.3 DISTRIBUTION 3 | 6.0 REVIEW 3 | 1.0 INTRUDUCTION | THE EXISTENCE OF SOUND FORMAL TECHNICAL MANAGEMENT SYSTEM IS A PREREQUISITE TO | A COMPREHENSIVE MANAGEMENT SYSTEM INVOLVES DEFINING THE POLICY | SETTING | OBJECTIVES | AND ESTABLISHING METS FOR MONITORING THE PLANT PERFORMANCE AND | INITIATING CORRECTIVE ACTION WHERE DEFICIENCIES ARE IDENTIFIED. | IT IS IMPORTANT THAT THE POLICY AND OBJECTIVES OF THE COMPANY ARE CLEARLY | UNDERSTOOD BY ALL THE STAFF WITHIN THE COMPANY. IT IS ESSENTIAL THEREFORE | POLICY | AND MONITORING METS ARE ADEQUATELY DETAILED WITHIN THE | RELEVANT DIVISIONAL FORMAL DOCUMENTATION SYSTEMS. | SERVICES DIVISION AND ALL STATIONS. | ISSUE01 | REV: 01 DEC 2019 | REDRAFTED WITH NECESSARY CORRECTION AND SENT TO NEW FORMAT. IN STRUCTURE | MANAGER” REPLACED WITH “ OF PROJECT”. | 5.0 STRUCTURE | THE TECHNICAL MANAGEMENT SYSTEM INVOLVES TWO SPECIFIC LEVELS OF AUTHORITY | NAMELY: | THE COMPANY PROCEDURES | AS NECESSARY | TO DETAIL A STRATAGEM IN THE FORM OF DIRECTIVES AND GUIDANCE NOTES THAT WILL | SPECIFIC DIRECTIVES AND GUIDANCE NOTES WILL ALSO BE NEEDED TO | ADDRESS SPECIFIC TECHNICAL MATTERS AND PROBLEMS IDENTIFIED DURING POWER | GENERATION. | THE STATUS OF DIRECTIVES WILL BE MANDATORY AND WILL REQUIRE AUTHORIZATION BY THE | 5.2 POWER STATIONS | THE OF PROJECT AT EACH POWER STATION WILL ISSUE INSTRUCTIONS CONTAINING | WHILST ACKNOWLEDGING THE SITESPECIFIC NATURE OF THESE INSTRUCTIONS. | THE INSTRUCTIONS ISSUED BY EACH OF PROJECT WILL THEREFORE | BY DEFINITION BE | WHICH WILL INSTRUCT STATION STAFF ON STATION | SITESPECIFIC | MANDATORY DOCUMENTS | POLICY. | COORDINATING AND PREPARATION AND APPROVAL OF THE SAME. THE APPROVED COPIES | SHALL BE LOADED IN SITE INTRANET AS WELL AS COS WEB. | THE PREPARATION AND REVISION OF LMI’S SHALL BE DONE BY CORRESPONSINF SECTIONAL | ’S. | 5.3 DISTRIBUTION | THE DOCUMENT ONCE APPROVED SHALL BE UPLOADED IN SIMHADRI INTRANET AND HARD | 6.0 REVIEW | 912558 | 12:45:55 | D15 | 202412:45:55 | AND BOILER FILL PUMPS: O | 009 HAS BEEN MADE AS PER THE NEW TC DOCUMENT | 021 REV. NO.: 0 APPROVED ON 31 JAN. 2024 AND FOLLOWING HAS BEEN | INCORPORATED. | S. NO NEW CHANGES DONE AS PER | MONITORING FREQUENCY OF BFP OILS HAVE BEEN | 1. OGN | 021 REV. NO.: | 0 NOV. 2023 | SECTION 5.0 PAGE NO.6 | TURBINE LUB OIL SPECIFICATIONS | 2 ANNEXURE 1 OGN | PAGE NO.10 | PAGE NO.9 | LUB OIL FLUSHING CLEARANCE PARAMETERS POST | AOH SEPARATE SECTION INCORPORATED. | SECTION 6.0 PAGE NO.7 | NONCOMPATIBILITY OF TURBO GENERATOR | OILS SUPPLIED BY DIFFERENT OIL COSISO00 | LUBRICATING | 4 COMPANIES. OGN | SECTION 7.0 PAGE NO.7 | RECORDS TO BE MAINTAINED FOR ANALYSIS AND TOP | UP HAS BEEN INCORPORATED. | 5 OGN | SECTION 8.0 PAGE NO.8 | COMPLIANCE CHECKLIST IS INCORPORATED. | ANNEXUREIII | PAGE NO.12 | COMPARISON TABLE BETWEEN NAS AND ISO HAS | BEEN INCORPORATED. | 6 OGN | ANNEXURE – IV PAGE NO.13 | SUBMITTED FOR KIND APPROVAL AND IMPLEMENTATION. | 15:53:37 | 16:26:04 | 16:46:30 | PUMPS" | BOILER FEED PUMPS" | PLEASE REVIEW. | 17:13:51 | REVIEWNED AND NO CHANGES PROPOSED IN THE DOCUMENT. | TITLE OF THE LMI CORRECTION MAY BE DONE. | FORWARDED FOR FURTHER APPROVAL. | 18:02:56 | TITLE OFN THE LMI MAY PLEASE BE CORRECTED. FORWARDED FOR FURTHER APPROVAL. | 18:19:56 | 10:33:39 | PUT UP FNOR APPROVAL | 07:18:43 | 15:24:47 | LOCATION MANAGEMENT INSTRUCTION LMI | ISSUE NO: 02 | DATE: 01 FEBRUARY 2024 | REVISION 04 | PREPARED BY V.LALITHADEVI DY MANAGER CHEM | CHECKED BY PIYUSH SRIVASTAVA AGM CHEM | CHECKED BY NAVIN KISHORE AGM TMD | REVIEWED BY D P PATRA GM O | APPROVED BY S.K. SINHA HOP | CHEM009 | ISSUE 002 | REVISION: 04 PAGE 1 OF 13 | S.NO DESCRIPTION PAGE NO | 4.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED 35 | 6.0 PARAMETERS MONITORING POST ANNUAL OVERHAULING 7 | 7.0 NONCOMPATIBILITY OF OILS SUPPLIED BY DIFFERENT OIL COMPANIES 7 | 8.0 RECORDS TO BE MAINTAINED 8 | ANNEXUREI TURBINE LUBRICATING OIL SPECIFICATIONS SUBCRITICAL 910 | UNITS | ANNEXUREII INTERPRETATION CHART OF TESTING PARAMETERS 1112 | ANNEXUREIII COMPLIANCE CHECKLIST 1213 | ANNEXUREIV COMPARISON TABLE BETWEEN NAS AND ISO 13 | 9.0 REVIEW 13 | REVISION: 04 PAGE 2 OF 13 | THE TURBINE LUBRICATING OIL MUST WITHSTAND CONTINUOUS THERMAL CYCLING AND A VARIABLE DEGREE OF | SLUDGE | WATER | HYDROGEN AND AIR. IT IS REQUIRED TO RELEASE READILY SUCH | CONTAMINATION BY SOLID PARTICLES | CONTAMINANTS AND RETAIN ITS LUBRICATING AND OTHER PROPERTIES OVER VERY LONG PERIODS AS TOTAL REPLACEMENT | OF OIL IS PROHIBITIVELY COSTLY. | IN ORDER TO MEET THE ABOVE OBJECTIVES | 009 REVISION03 DATED MAY2022 | IN ORDER TO PROVIDE ASSURANCE THAT THE OIL IS BEING MAINTAINED IN A HEALTHY CONDITION | IT IS NECESSARY TO | MONITOR SELECTED PROPERTIES OF THAT OIL. | THIS LMI DEFINES LIMITS FOR VARIOUS PARAMETERS AND FREQUENCY OF TESTING OF OILS SO THAT DEGRADATION IN | SERVICE DOES NOT RESULT IN UNDUE THREAT TO THE MACHINE. | 4.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED | NEW OIL | 4.1 ALL SUPPLIES SHOULD EITHER BE DELIVERED WITH A BIS MARKING ALONG WITH THE CHEM | SAMPLES TMD | MARKING IS NOT AVAILABLE | PROCUREMENT SPECIFICATION. IF BIS CERTIFICATE | MAY BE TAKEN AND EXAMINED FOR APPEARANCE AND VISCOSITY BEFORE TOPPING UP. | ALL SAMPLES SHOULD BE WITHIN THE PERMITTED VISCOSITY RANGE AND SHOULD APPEAR | CLEAR AND BRIGHT AND VISUALLY FREE | FROM SOLID AND LIQUID CONTAMINANTS. | 4.2 IN THE EVENT OF A DISAGREEMENT OVER THE APPEARANCE OF THE OIL SAMPLES THE CHEM | PRESENCE OF CONTAMINANTS SHALL BE DETERMINED. MAXIMUM CONCENTRATIONS OF | 0.0007% WEIGHT BY WEIGHT 7MG | 7MG | PROCEDURE FOR OIL: COSISO00OIN | 015”. | OIL IN SERVICE | 4.3 TURBINE OILS WILL GRADUALLY DETERIORATE IN SERVICE DUE TO OXIDATION AND THE OPN | OPN | PRESENCE OF WATER | CORROSION AND WEAR PRODUCTS. PURIFYING EQUIPMENT I.E. | CENTRIFUGE ETC. SHOULD BE PRESSED INTO SERVICE TO MAINTAIN THE QUALITY OF THE | OIL SUPPLIED TO THE BEARINGS. | REVISION: 04 PAGE 3 OF 13 | 4.4 SAMPLING AND MONITORING SHOULD BE CARRIED OUT ON A REGULAR BASIS TO ASCERTAIN CHEM | THE RATE OF DETERIORATION AND TO ENABLE NECESSARY CORRECTIVE MEASURES TO BE | TAKEN. | DELIVERED TO THE MACHINE SHOULD BE OBTAINED FROM ANY CONVENIENT POINT | PREFERABLY FROM TURBULENT FLOW AREAS SUCH AS TURBINE BEARING RETURN LINES | WHEN THE OIL IS IN CIRCULATION | AND TESTED AS SPECIFIED IN TABLEII. | DURING THE TURBINE LUB OIL FLUSHING CHEM | WHEN THE UNIT IS COMING AFTER OVERHAULING | ACTIVITY | OIL SAMPLES SHOULD BE TAKEN FROM OIL TANK INLET AND OUTLET LINE FOR | MONITORING THE PARAMETERS AND CLEARANCE IS TO BE ACCORDED AS PER THE LIMITS | SEC 10.0 | MENTIONED IN TABLEIII SEC 10.0. | IT MAY BE DESIRABLE TO OBTAIN SAMPLES AT DIFFERENT POSITIONS IN ORDER TO TRACE | SOURCES OF CONTAMINATION AS PER THE REQUIREMENT. FOR DETAIL SAMPLING | TESTING PROCEDURE FOR OIL: COSISO00OIN | 015” | SHOULD BE | REFERRED TO. | 4.6 WATER | DIRT | HYDROGEN AND AIR SHOULD BE REMOVED FROM THE OIL AS EFFICIENTLY AND TMD | AS QUICKLY AS THE SYSTEM DESIGN ALLOWS USING THE INSTALLED PURIFICATION | EQUIPMENT. IT IS DESIRABLE TO USE CONDENSATE OR DEMINERALIZED WATER FOR | C IS NORMALLY REQUIRED TO BREAK OIL | OR DIRTY OIL | WATER EMULSIONS. WET AND | RETURNED TO THE TURBINE WILL EVENTUALLY MANIFEST ITSELF IN CORROSION | WEAR | MALFUNCTIONING OF THE EQUIPMENT AND BIOLOGICAL GROWTH. | OIL EMULSION SHOULD BE DRAINED FROM THE MAIN OIL TANK DRAIN OPN | 4.7 WATER AND WATER | AT INTERVALS TO ENSURE THAT A LOW LEVEL OF WATER IS MAINTAINED IN THE TANK. | ACCUMULATED WATER OR WATER OIL EMULSION SHALL BE DRAINED FROM LOWEST DRAIN OF | THE MAIN OIL TANK AT | AVAILABLE OPPORTUNITIES LIKE UNIT SHUT DOWN. | 4.8 CENTRIFUGE SHOULD BE IN SERVICE WITH HEATER TEMPERATURE SET AT 65 80 DEG C TO OPN | BREAK OIL EMULSION. HEATER TEMPERATURE SHOULD NOT EXCEED 80 DEG C TO AVOID | OXIDATION OF OIL. IT IS DESIRABLE TO USE CONDENSATE OR DEMINERALIZED WATER FOR | SEALING CENTRIFUGES. VAPOR EXTRACTION FANS SHALL BE IN SERVICE CONTINUOUSLY TO | REMOVE | ANY MOISTURE VAPORS. | REVISION: 04 PAGE 4 OF 13 | OM CHEM | 358091 | 202420:32:20 | 20:32:20 | SUBJECT:THE REVISION OF LMI ON SAFETY PRECAUTIONS FOR HANDBLING | BULK ACID CAUSTIC SODA AND SODIUM CHLORITE O | 007 ON SAFETY PRECAUTIONS FOR HANDLING BULK | THE LMI | M CHEM SECTION HAS BEEN | CAUSTIC SODA AND SODIUM CHLORITE PERTAINING TO O | REVIEWED AND REVISED. CHANGES MADE ARE MENTIONED IN THE BELOW TABLE. | CURRENT ISSUE AND REVISION | PARA NO REVISION DETAILS REASON FOR REVISION | DETAILS OF LMI | · SAFETY ASPECTS FOR | UNLOADING OF | HANDLING | HYDROCHLORIC ACID | CAUSTIC | SODA | LYE | AND SODIUM CHLORITE | HAVE BEEN SEGREGATED INTO SEPARATE LMI | SECTIONS. | OGN REVISED | STORAGE REQUIREMENTS OF ISSUE NO: 08 | PUMPS HAVE BEEN COSISO00 | ALKALI TANKS | INTRODUCED. OGN | MAY | REV. NO.: 06 | DATE: 29072024 | JSA FOR RUBBER LINING JOB OF | · SOP | 2024 | BULK ACID STORAGE TANK HAVE BEEN | INCORPORATED IN THE DOCUMENT. | · TITLE OF DOCUMENT REVISED FROM | SAFETY PRECAUTIONS FOR HANDLING | BULK ACID AND CAUSTIC SODA | ANNEXURE | VIII. · GENERAL REQUIREMENTS FOR | UNLOADING ACID | ALKALI BY GRAVITY | BEEN ADDED | · STORAGE | HANDLING OF CAUSTIC | SODA FLAKES ADDED | 8.0 | SUBMITTED FOR KIND APPROVAL PLEASE | 18:50:33 | PLEASE RNEVIEW AS DISCUSSED. ANY DEVIATION FROM OGN TO BE MENTIONED AND JUSTIFIED IN LMI AND APPROVAL | NOTE. | 18:07:31 | AS DISCNUSSED PLEASE REVIEW. | 10:40:48 | 11:45:06 | LMI REVNISED ACCORDINGLY. SUBMITTED FOR APPROVAL. | 11:58:21 | 18:39:04 | 11:31:20 | 11:41:08 | REVISEDN AS PER STANDARD FORMAT. | 16:35:13 | 16:45:42 | 17:17:38 | 17:44:40 | IN LMIN | ACTIVITY SL NO5 SUB CLAUSE4. | IN IDENTIFICATION OF PIPELINE. | हमे न्त सैनी विरष्ठ प्रबंधक | HEMANT SAINI 100407 SENIOR MANAGER | 9425284675 | HEMANTSAINI@NTPC.CO.IN | 18:59:35 | PAINTING SHALL BE | AS PER NPREPAGE NOTINGS | DONE BY CPC GROUP. | SUBMITTED PLEASE. | 11:24:49 | 17:00:05 | REVIEWNED AND FOUND IN ORDER. | शिलनी िसह उप महाप्रबंधक | SHALINI SINGH 008621 DY. GENERAL MANAGER | SHALINISINGH01@NTPC.CO.IN | 9650991330 | 17:56:25 | 18:50:09 | DETAILS NOF REVISIONS TO BE ADDED IN THE LMI | 18:02:57 | MAY PLENASE ADD THE DETAIL OF REVISIONS IN THE LMI. | 19:28:36 | 661269 | 11:21:38 | D11 | 202411:21:38 | SUBJECT:CHEMICAL CONTROL OF GENERATOR STATOR PRIMABRY | WATER SYSTEM O | 002 ON CHEMICAL CONTROL OF GENERATOR STATOR PRIMARY WATER SYSTEM PERTAINING | THELMI | M CHEM SECTION HAS BEEN REVIEWED AND REVISED. CHANGES MADE ARE MENTIONED IN THE BELOW TABLE. | TO O | S. NO CLAUSE REVISION 8 REVISION 9 | NEW LINE ADDED: | 6.0 | THE SAMPLE LINE SHOULD HAVE TWO | NUMBER ISOLATING VALVES. | AN ONLINE DO ANALYZER SHALL BE | INSTALLED IN LOWDO GENERATOR STATOR | 2. 7.1 WATER SYSTEM FOR CONTINUOUS | MONITORING OF THE DISSOLVED OXYGEN IN | THE STATOR PRIMARY WATER | 3. 9.2.3 <0.10 KG | CM2 THEN N2 GAS TOP | PRESSURIZATION IS TO BE DONE | SPARE RESIN STRAINERS SHOULD BE | 4. 9.2.12 | AVAILABLE FOR SPU SYSTEM | FEEDBACK OF NAOH DOSING PUMP | 5. 9.2.16 SHOULD BE AVAILABLE IN UNIT CONTROL | ROOM | SPU | ION EXCHANGER SPU OUTLET | STATOR WATER | CONDUCTIVITY TREND | CONDUCTIVITY ARE ALSO TO BE | 6. 9.2.18 CONDUCTIVITY ARE ALSO TO BE MONITORED | MONITORED AND RECORDED IN | AND RECORDED IN GENERATOR STATOR WATER | GENERATOR STATOR WATER LOGBOOK | LOGBOOK ONCE | DAY | ONCE | SHIFT | SODA LIME FILTER OF NAOH TANK | ALKALI TANK SODA FILTER IS TO BE REPLACED | 7. 9.2.24.2 SHOULD BE CHANGED AS PER OEM | YEAR | ADDED: | 8. 10.4 THE STATOR WATER SAMPLE TO BE CROSS | ICP | CHECKED THROUGH IC | AAS | SIX MONTHS FOR TOTAL COPPER | 9. 10.5 | RECORD | SODA LIME FILTER CHANGEOVER | ELECTRICAL | CPU RESINS CATION IN H FORM AND | ANION IN OH FORM SHOULD BE USED IN | IF THE | THE SPU SYSTEM. HOWEVER | CPU RESINS CATION IN H FORM | STATION IS FACING ANY ISSUE IN THE SPU | 10. ANNEXURE 1. NOTE: AND ANION IN OH FORM SHOULD | THEN | PERFORMANCE WITH CPU RESINS | BE USED IN THE SPU SYSTEM. | STATION SHOULD USE ONLY OEM | M MANUAL FOR DETAILS | GENERATOR STATOR WATER FLOW | WINDING | H2 GAS PRESSURE | SPU FLOW AND N2 | 11. ANNEXURE 1 DP | ARE ALSO TO BE RECORDED IN THE | LOGBOOK’ ALONG WITH THE ABOVE RESULTS. | 12. ANNEXURE 2 | ADDED STANDARD PI TAG LIST FOR STATOR | 13. ANNEXURE5 | PRIMARY WATER SYSTEM IN ANNEXURE5 | SUBMITTED FOR KIND APPROVAL PLEASE. | मयंक िबष्ट सहायक प्रबंधक | ASSISTANT MANAGER | MAYANK BISHT 105268 ASSISTANT MANAGER | MAYANKBISHT@NTPC.CO.IN | 8077371841 | THE LMI ON THE ABOVE TOPIC IS REVIEWED AND REVISED. ALL RELEVANT | BASED ONN THE REVISION OF ORIGINAL OGN | CHANGES ARE MADE IN THE LMI AND LISTED ACCORDINGLY. | SUBMITTED FOR REVIEWING THE DOCUMENT AND SUBSEQUENT APPROVAL BY COMPETENT AUTHORITY PLEASE. | 18:41:57 | 1. INN CLAUSE 9.2 'MONITORING | CONTROL' | FOLLOWING CHANGES MAY BE DONE: | CPC | AHD | SL. NO.11: ADD C | SL. NO.16: ADD C | SL. NO.24.2: ADD TMD | TMD IN CHEKING. | 19:43:12 | LMI REVNISED ACCORDINGLY. SUBMITTED FOR APPROVAL | 17:25:01 | 11:23:23 | 16:15:54 | 15:09:59 | REVIEWEND | 15:44:29 | 10:08:20 | ADDITIONAL POINTS TO BE ADDED. | SOLUTION. | 10:33:41 | 10.5 CONRRECTIONS DONE | RECORD KEEPING OF NAOH TANK LEVEL IS MENTIONED IN 9.2.17 | 11:21:10 | BE DONE BY EM AS BEING FOLLOWED IN REPLACEMENT OF SPU RESIN. | 12:56:58 | 16:14:19 | THE CHANNGES ARE MADE IN THE LMI ACCORDINGLY. MAY PLEASE PROCESS THE PROPOSAL. | 11:34:09 | THE LMNI IS REVIEWED AND FOUND IN ORDER WRT EM. | 12:06:38 | 19:41:53 | REVIEWNED AND IS BEING FORWARDED FOR FURTHER PROCESS PLEASE. | 15:22:14 | MAY PL NREVIEW THE LMI DOCUMENT | 18:41:46 | सुनेता साहा उप महाप्रबंधक | SUNETA SAHA 006843 DY. GENERAL MANAGER | 9434737713 | SUNEITASAHA@NTPC.CO.IN | 19:23:20 | 109306 | D17 | 18:35:38 | 202218:35:38 | SUBJECT:REVIEW OF LMI RESIDUAL LIFE AND CONDITION ASSESSMENT OF RCBC AND | 013 O | STEEL STRUCTURES W.R.T. LMI | THE LMI OF "RESIDUAL LIFE AND CONDITION ASSESSMENT OF RCC AND STEEL STRUCTURES" WITH REF. | REV. NO.02 WAS PREPARED AND APPROVED IN THE MONTH OF MAY'2020. | THE ABOVE LMI HAS BEEN REVIEWED AS ON DATE AND REVISION 03 ENCLOSED. NO CHANGES IN LMI ARE | THE LMNI OF "RESIDUAL LIFE AND CONDITION ASSESSMENT OF RCC AND STEEL STRUCTURES" WITH REF. | REV. NO.3 ATTACHED MAY PLEASE BE APPROVED FOR IMPLEMENTATION. | 16:56:17 | 19:21:59 | COMPENTENT AUTHORITY MAY APPROVE THE LMI REVIEWED | 09:04:13 | PLEASE DNISCUSS THIS LMI | WITH UNDERSIGNED. | 19:48:26 | DISCUSSNED. MAY PLEASE BE FORWARDED FOR APPROVAL. | 10:57:47 | THE LMNI REVISION MAY PLEASE BE ACCORDED APPROVAL. | 18:45:37 | 20:10:34 | 09:15:23 | REV. NO. : 03 MAY 2022 | LMI FOR RESIDUAL LIFE AND CONDITION | ASSESSMENT OF RCC AND STEEL | STRUCTURES | 1. TITLE OF LMI LMI FOR RESIDUAL LIFE AND CONDITION ASSESSMENT OF RCC | AND STEEL STRUCTURES | DATE ISSUE1; REV.3; MAY’2022 | REV.NO.:0 DECEMBER 2011 | 4. PRERPARED BY NAME: SHRI. PANDAB DATTA | 5. CHECKED BY NAME: SHRI. JAYANTHI GOPI KIRAN | NAME: SHRI. ASIS KUMAR MUKHOPADHYAY | NAME: SHRI. MATHEW EIPE KOVOOR | 6. REVIEWED BY GM MAINT. | MAINT. | NAME: SHRI. RAJESH KUMAR JHA | NAME: SHRI. GIRISH CHANDRA CHOUKSE | 7. APPROVED BY GGM SIMHADRI | 9. INDEX LIST ENCLOSED. | 10. DISTRIBUTION LIST ENCLOSED. | TITLE: LMI FOR RESIDUAL LIFE AND CONDITION ASSESSMENT OF RCC AND STEEL STRUCTURES | REV:03 DATE: MAY’2022 | PAGE: 3 OF 9 | 2. SCOPE 4 | 3. REFERENCE DOCUMENT 4 | 4. SUPERSEDED DOCUMENT 4 | 5. PRACTICES TO BE FOLLOWED | FOR CONDITION 45 | ASSESMENT | 6. RESPONSIBLITIES 6 | 7. RECORD KEEPING 6 | 9. DISTRIBUTION LIST 7 | 10. REVISION INDEX 8 | 11. COMPLIANCE RECORD 9 | PAGE: 4 OF 9 | REINFORCED CONCRETE AND STEEL | TO SEA AND SEA WATER IS USED FOR COOLING AND ASH WATER SLURRY PURPOSES | STRUCTURES OF PLANT UNDERGO DEGRADATION DUE TO CORROSION SUSCEPTIBILITY | IMPACT OF ENVIRONMENT SUCH | CHEMICAL ATTACK | ABRASION ETC. TO MITIGATE ANY RISK OF CATASTROPHIC FAILURE | AGED | AS WEATHERING ACTION | STRUCTURES OF COASTAL BASED PLANTS REQUIRE STRUCTURAL INTEGRITY ASSESSMENT PRIMARILY ON NEED BASIS. | THE SCOPE OF THIS LMI IS TO DETAIL THE VARIOUS TESTS TO BE CARRIED OUT IN CONCRETE STRUCTURES | STRUCTURES AND MACHINE FOUNDATIONS THEREBY ENHANCING THE FUNCTIONAL LIFE OF POWER PLANT BY | A IDENTIFICATION OF RCC AND STEEL STRUCTURES' HEALTH DEFICIENCIES COVERING ALL AGING AND | CONTINUOUS AND CYCLIC | CORROSION OF STEEL | DEGRADATION ASPECTS VIZ: CARBONATION OF CONCRETE | ENVIRONMENTAL IMPACTS | CONCRETE | SHRINKAGE | TEAR | CREEP | LOADING OF STRUCTURE | DEGRADATION | FIRE ACCIDENTS ETC. | MODIFY | B BASED ON THE RESULTS OF ASSESSMENT STUDIES AN ENGINEERING SOLUTION TO REPAIR | REBUILD | ALONG WITH THE BASIS THEREOF INCLUDING IN TERMS OF COST ECONOMICS WITH VARIOUS OPTIONS SUGGESTED | FOR IMPLEMENTATION. | 3.0 REFERENCE DOCUMENT | 4.0 SUPERSEDED DOCUMENT | 013 OF REV01 | 5.0 PRACTICES TO BE FOLLOWED FOR CONDITION ASSESMENT | CONCRETE STRUCTURES | 1 ASH HANDLING BUILDINGS INSPECTION REPORT O | RHT | CST | CMT | 2 WTP BUILDINGS | UPVT | HCPT LMI | CHIMNEY LMI | 3 NDCT | 005 TO BE | REVIEWED EVERY | WAGON | 4 TRACK HOPPER | TIPPLER TUNNELS | ALL OTHER TESTS ARE | NEED BASED | 5 SEA WATER PUMP HOUSE | DEPENDING ON THE | JETTY | ABOVE INSPECTION | REPORT. | MACHINE FOUNDATIONS | INSPECTION REPORT | 1 TG DECK FOUNDATION OF | TDBFP | 2 BFP | 011 TO BE | FOUNDATION | 3 MILL FOUNDATIONS YEAR. | HCPT | 4 PA FAN FOUNDATIONS | DYNAMIC | 5 FD FAN FOUNDATIONS ANALYSIS | 6 ID FAN FOUNDATIONS MEASUREMENT OF | AMPLITUDE | FREQUENCY OF | VIBRATIONS | NATURAL | FREQUENCY OF NEED BASED | FOUNDATION SYSTEM | SIGNATURE ANALYSIS OF ABOVE INSPECTION | BLOCK FOUNDATION REPORT. | DECK SLAB OF | ID FAN | ETC | CUT AND | PULL OUT CAPO | TEST | STEEL STRUCTURES | 1 TG HALL STRUCTURES INSPECTION REPORT O | 2 EOT CRANE STRUCTURES | 3 BOILER AND AUXILLARIES CIV | 4 BOILER SUPPORTING CARRY OUT VARIOUS | DPT | TESTS LIKE VI | UT YEAR | 5 BOILER COLUMN FOUNDATION MPI | 6 ESP AND DUCT SUPPORTING | 7 CHIMNEY SHELL LINER NEED BASED | MCHP | M-CHP | 8 CHP CRUSHER HOUSE | CONVEYOR GALLERIES | REPORT | TRANSFER POINTS | PAGE 1 OF 18 | STORES | 12345678 | 986877 IDATE:31 | 12:38:18 | 202312:38:18 | SUBJECT:LMI FOR 202324 O | PRESERVATION | ISSUE NO. 01 | VIDE REFERENCE: LMI | MAR 2023 HAS BEEN REVIEWED AND REVISED. | NO.1 | FOLLOWING CHANGES HAVE BEEN DONE IN THIS REV. NO.1. | 1. ENTIRE DOCUMENT CHECKED AND CORRECTED. EXISTING INFORMATION IN COSISO00OGN | 017 | 2. ELECTRONIC APPROVAL OF LMI IN PRADIP FILE MANAGEMENT SYSTEM HAS BEEN INCORPORATED. | 3. PROCEDURE FOR DISTRIBUTION OF LMI HAS BEEN REVISED AS FOLLOWING: “SOFT COPY OF THE LMI SHALL BE | UPLOADED IN THE LAN BY THE ISSUING AUTHORITY THROUGH A | LINK EDIT PROTECTED THROUGH PASSWORD. THE UPLOADED SOFT COPY OF THE DOCUMENT IS TO BE CONSIDERED AS | CONTROLLED COPY. COPY OF THE DOCUMENT CAN BE DISTRIBUTED THROUGH E MAIL” | PAGE 2 OF 18 | मधु बाबू आवार् उप प्रबंधक | DEPUTY MANAGER | MADHU BABU ARAVA 035200 DEPUTY MANAGER | 9493906039 | MBARAVA@NTPC.CO.IN | 986877 | 16:47:30 | 17:09:29 | PAGE 3 OF 18 | 18:55:56 | ALL MAINNTENANCE T. S ARE REQUESTED TO KINDLY STUDY THE PROPOSED REVISION OF THE LMI SEE | SHALL BE RECORDED AND CASE FILE SENT TO CENTRAL | ANNEXURE AND APPROVE THE SAME. ANY CHANGES IF REQUIRED | STORES FOR THE NECESSARY REVISION IN THE PROPOSED LMI. | WHO SHALL CARRYOUT PERIODIC VIST OF STORES FOR CHECKING THE PRESERVATION OF SPARES STORED THEREIN. | 10:47:16 | PAGE 4 OF 18 | CHANGES | CORRECTION | टी.आर. राजगोपालन् अपर महाप्रबंधक | TR RAJAGOPALAN 003994 ADDL. GENERAL MANAGER | FOLLOWINNG POINTS MAY BE ADDED W.R.T. C | I SPARES: | 1. STORAGE OF ACCUMULATOR BLADDERS: | IN HANGING POSITION. | • IT SHOULD BE KEPT IN AC ROOM | • FOLDING IS TO BE COMPLETELY AVOIDED TO PREVENT DEFORMATION. | • PRESSURE INSIDE BLADDERS SHOULD BE KEPT> 0.1 BAR | 2. RUBBER SEAL KITS | ORINGS TO BE KEPT IN AC ROOM IN ORIGINAL PACKING. | IN ORIGINAL PACKING | प्रदीप कुमार मौयर् विरष्ठ प्रबंधक | PRADEEP KUMAR MOURYA 100966 SENIOR MANAGER | PRADEEPMOURYA@NTPC.CO.IN | 9650995380 | 10:09:00 | PAGE 5 OF 18 | EQUIPMENT ATTACHED WITH THIS NOTE TO BE FOLLOWED. | 10:37:57 | PAGE 6 OF 18 | AS PER NLATEST OGN ON LONG TERM STORAGE OF POWER PLANT EQUIPMENTS | W.R.T C | • RUBBER ITEMS LIKE SEALS | ORINGS ETC. SHOULD BE STORED IN AC STORE. CLAUSE 4.15 | DIAPHRAGMS | CLAUSE | 11 OF OGN. | 18:45:31 | PAGE 7 OF 18 | REVIEWNED AND PUT UP FOR APPROVAL PLEASE. | 23:02:43 | 10:26:41 | PAGE 8 OF 18 | 16:23:41 | PLEASE INNCLUDE IN ANNEXURE1 SL.NO. 13 "CONTROL AND INSTRUMENTATION" THE FOLLOWING ELECTRONIC SPARES OF | TO BE KEPT IN AC ROOM: | 1. VFD | DC DRIVE SPARES OF M | S SIEMENS | 2. PROXIMITY SENSORS | S SCHNEIDER | 3. PLC CARD SPARS OF M | 4. PULL CHORD CONTROLLERS OF M | S PARAMETRICS | 5. ELECTRONIC SPEED MONITORING UNITS | S JAYASHREE | SPEED SENSOR PROBES OF M | BATTERY CHARGERS. | 6. SPARES OF UPS | 09:31:25 | PAGE 9 OF 18 | MAY RENVIEW | 15:45:27 | FORWARDED FOR FURTHER APPROVAL | REVIEWEND FOR HT MOTORS AND TRANSFORMERS | FOUND IN ORDER | 16:03:29 | PAGE 10 OF 18 | IN LMIN ANNEX 1 | EM MAY BE ADDED. | ITEM 13 AND 22 | PRESERVATION OF RUBBER ITEMS ITEM 22. | ITEM 22 | RUBBER ITEMS SHOULD BE STORED IN AC ROOM BY APPLYING A COAT OF TALCUM POWDER ON THE CORDS AND GASKETS. | ITEM 13 | PRESERVATION OF ELECTRONIC ITEMS ITEM 13. | THE PHILOSOPHY OF PRESERVING THE ELCTRONIC CARDS IS SAME AS BEING DONE FOR C | I ITEMS. | 09:47:41 | ASH DYKE MANAGEMENT | ASH DYKE MGM | 1093251 | 11:22:25 | 202511:22:25 | SUBJECT:GUIDELINES FOR ASH DYKE MANAGEMENT LMI APPRBOVAL | REG. O | AS PER THE OGN REF. COSIS000OGN | 022 WAS PREPARED. | 022 | VER 4 | THE SAID LMI HAS BEEN REVISED AS PER THE REVISED OGN VER 4 RELEASED IN MARCH 2025. | "GUIDNELINES FOR ASH DYKE MANAGEMENT LMI "HAS BEEN REVISED AS PER THE REVISED OGN VER 4 | RELEASED IN MARCH 2025.THIS HAS BEEN CHECKED AND FOUND OK. | SUBMITTED FOR APPROVAL FROM COMPETENT AUTHORITY | अमरेन्द्र कुमार रमन उप महाप्रबंधक | AMRENDRA KUMAR RAMAN 100146 DY. GENERAL MANAGER | AKRAMAN@NTPC.CO.IN | 9473199165 | 12:13:13 | PLEASE RNEVIEW AS DISCUSSED. | 11:04:16 | DOCUMNENT UPDATED BASED ON DISCUSSION. | 16:44:30 | 16:59:58 | PARAGRANPH NUMBERS MAY PLEASE BE CHECKED AND REVISED FROM PAGE54 TO PAGE61. | 16:36:08 | PARAGRANPH NUMBERING HAS BEEN REVISED FROM PG. 54 TO 61. ADDITIONALLY | LAYOUT IN ANNEXURED HAS ALSO BEEN | UPDATED CORRESPONDING TO SIMHADRI ASH DYKE. | 16:27:26 | 21:46:27 | 17:09:30 | REVIEWNED FOR AHD AND FOUND IN ORDER. | क्रािंतकुमार कुरबा विरष्ठ प्रबंधक | KRANTHIKUMAR KURBA 102735 SENIOR MANAGER | KRANTHIKUMAR@NTPC.CO.IN | 9448290390 | 19:07:26 | 11:31:14 | ड़ॉ वी ज़यन अपर महाप्रबंधक | VELAYUDHANPILLAI JAYAN 006202 ADDL. GENERAL MANAGER | ENVT. MGT. | VJAYAN@NTPC.CO.IN | 9650991721 | 11:51:46 | EMG | रोिहत िसह उप महाप्रबंधक | ROHIT SINGH 009359 DY. GENERAL MANAGER | 9650994838 | ROHITSINGH01@NTPC.CO.IN | 17:55:28 | डॉ वी ज़यन अपर महाप्रबंधक | 18:09:41 | REVIEWNED THE LMI AND FOUND IN ORDER | तुषार कानूनगो अपर महाप्रबंधक | TUSHAR KANUNGO 007981 ADDL. GENERAL MANAGER | 9437960590 | TUSHARKANUNGO@NTPC.CO.IN | 11:37:51 | 10:25:27 | 20:09:39 | 18:59:54 | LMI REVNIEWED AND FORWARDED FOR APPROVAL. | 16:24:42 | 10:34:10 | 11:07:50 | 17:45:06 | CIDCS | 367682 | 202416:51:50 | 16:51:50 | SUBJECT:REVISION OF LMI ON SECURITY POLICIES FOR CONTRBOL | DDCMIS | LMI ON SECURITY POLICIES FOR CONTROL SYSTEMS DDCMIS HAS BEEN REVISED KEEPING IN VIEW OF HMI | 2*500 | UPGRADATION IN ST2 NTPC SIMHADRI 2*500 AND ADDITION OF MEMBER IN INFORMATION SECURITY TEAM. | I004_REV01 AND REVISED LMI IS ATTACHED FOR REFERENCE. | LMI ON SECURITY POLICIES OF CONTROL SYSTEM DDCMIS SMPPISO00LMI | 004 REV04 IS | SUBMITTED TO COMPETENT AUTHORITY FOR KIND APPROVAL. | 10:29:52 | MAY PL NREVISE AS DISCUSSED | 17:48:38 | REVISEDN COPY ATTACHED HEREWITH. | 16:13:17 | LMI ONN SECURITY POLICIES FOR CONTROL SYSTEMS IS SUBMITTED FOR APPROVAL | 16:25:53 | 17:11:54 | 09:17:55 | PLEASE CNONFIRM WHETHER FORMAT IS IN ORDER | 17:51:21 | PLS. CHENCK. | 11:34:15 | 16:18:10 | FRONT PNAGE OF LMI CHANGED AS PER STANDARD FORMAT.LMI NAME ALSO MODIFIED. | 16:24:21 | ATTACHEND LMI FILE IS AS PER SIMHADRI LMI FORMAT | 17:04:53 | LMI FONRMAT IS IN ORDER. | 18:02:35 | 07:15:43 | 17:59:01 | SECURITY POLICIES FOR CONTROL SYSTEMS DDCMIS | 004 REV. NO.:4 | AUGUST 2024 | 1 LMI NAME SECURITY POLICIES FOR CONTROL SYSTEMS DDCMIS | 3 REFERENCE DOCUMENT COSISO00OGN | 004 REV01 | REV NO: 3. | 4 SUPERSEDED DOCUMENT LMI | 5 AJEET KR RAUSHAN | PREPARED BY | SR. MANAGERC | 6 SHALINI SINGH | CHECKED BY | DGM C | 7 JAYAMOL RACHEL V | 8 SURESH JOHN DAVID | GMO | 9 SANJAY KUMAR SINHA | APPROVED BY | 2 SUPERSEDED DOCUMENTS 4 | 3 REVISION DETAILS 4 | 4 SECURITY POLICIES 4 | 4.1 INFORMATION SECURITY POLICY 4 | 4.2 FIRE WALL POLICY 5 | 4.3 INFORMATION IDENTIFICATION AND CLASSIFICATION POLICY 5 | 4.4 SECURITY POLICY REVIEW POLICY 6 | 4.5 INFORMATION LABELLING AND HANDLING POLICY 6 | 4.6 SYSTEM PLANNING AND ACCEPTANCE POLICY 6 | 4.7 CAPACITY MANAGEMENT POLICY 7 | 4.8 MEDIA HANDLING POLICY 7 | 4.9 INFORMATION SECURITY AWARENESS POLICY 8 | 4.10 THIRD PARTY ACCESS POLICY 9 | 4.11 CHANGE CONTROL POLICY 9 | 4.12 ANTI VIRUS POLICY 10 | 4.13 SYSTEM ACCESS POLICY 10 | 4.14 MONITORING POLICY 11 | 4.15 INCIDENT HANDLING POLICY 12 | 4.16 INFORMATION BACKUP AND RESTORATION POLICY 13 | 4.17 NETWORK ACCESS POLICY 14 | 4.18 USER ACCESS MANAGEMENT POLICY 14 | 5. AUDIT 15 | 6. REVIEW 15 | 7. REFERENCES 16 | 8. ANNEXURES 17 | 8.1 ANNEXURE 01: INFORMATION SECURITY TEAM 17 | 8.2 ANNEXURE 02: COMPLETE CONTROL SYSTEMS CONFIGURATION DIAGRAM 19 | 8.3 ANNEXURE 03: ASSET LIST 21 | 8.4 ANNEXURE 04: SECURITY AWARENESS PROGRAM 21 | 8.5 ANNEXURE 05: SECURITY AWARENESS TRAINING DETAILS 22 | 8.6 ANNEXURE 06: CHANGE REQUEST CR FORMAT 23 | 8.8 ANNEXURE 08: ANTIVIRUS UPDATE INFORMATION FORMAT 25 | 8.9 ANNEXURE 09: SYSTEM LOGS ABNORMALITY INFORMATION 26 | 8.10 ANNEXURE 10: INCIDENT HANDLING INFORMATION FORMAT 27 | 8.11 ANNEXURE 11: DATA BACKUP RECORD FORMAT 28 | 8.12 ANNEXURE 12: LIST OF SOP’S BACKUP | BACKUP | RESTORE | RESTORE 29 | 8.13 ANNEXURE 13: SCOPE OF WORK FOR AUDIT 30 | PAGE ¦ 3 | LMI NAME SECURITY POLICIES FOR CONTROL SYSTEMS DDCMIS | 004 REV NO: 04 | IN ORDER TO ENFORCE NETWORK SECURITY IN PLANT CONTROL SYSTEMS CONSISTING OF DDCMIS | SECURITY POLICIES AND PROCEDURES INCORPORATED HEREIN | SYSTEMS AND CONTROL NETWORKS | ARE TO BE FOLLOWED. | THESE SECURITY POLICIES | PROCEDURES ENVISAGE FORMATION OF AN INFORMATION SECURITY | TEAM. EVEN THOUGH DIFFERENT ROLES HAVE BEEN IDENTIFIED FOR THE INDIVIDUAL MEMBERS OF | THE INFORMATION SECURITY TEAM | MORE THAN ONE ROLE CAN BE PERFORMED BY THE SAME | PERSON. IT MAY BE NOTED THAT FOLLOWING POLICIES | GUIDELINES AND ADVISORY STEPS TO ENSURE MAXIMUM DATA SECURITY. | THE INTENT OF THIS LOCATION MANAGEMENT INSTRUCTION IS TO DOCUMENT THE POLICIES | BASED ON THE | TO BE ADOPTED FOR SECURING THE NETWORK AS WELL AS THE CONTROL SYSTEMS | REV NO:1 | CC OS IOM REF NO OSC | 05 VER 1.0 DATED 14.07.2021 . | SMPPISO00LMI | 3.0 REVISION DETAILS | 8.7 MODIFIED AS PER ST 2 HMI UPGRADATION |  ANNEXURES 8.1 |  ANNEXURE 8.13 SCOPE OF AUDIT REVISED AS PER THIRD PARTY AUDIT | 4.0 SECURITY POLICIES | THE POLICIES APPLY TO PLANT CONTROL SYSTEM NETWORKS AND TO THE ADMINISTRATORS | AND USERS OF THE SYSTEMS. | 4.1 INFORMATION SECURITY POLICY | 4.1.0 TEAM AN INFORMATION SECURITY TEAM MUST BE | ESTABLISHED TO INITIATE AND CONTROL THE | IMPLEMENTATION OF INFORMATION SECURITY WITHIN | CSLAN. THE TEAM SHALL INCLUDE CHAIRMAN | INFORMATION SECURITY MANAGER | INFORMATION | NETWORK | SECURITY COORDINATOR AND SYSTEM | DATABASE ADMINISTRATORS. | APPLICABLE ANNEXURES ANNEXURE1: TEAM MEMBERS | RESPONSIBILITIES | PAGE ¦ 4 | 12:49:57 | 226474 IDATE:27 | 202212:49:57 | SUBJECT:REVISION OF LMI BTL FAILURE ANALYSIS ANOD CONTROL | DATE: 27.06.2022 | SUBJECT: REVIEW OF LMI “BOILER TUBE FAILURE ANALYSIS AND CONTROL” | 049 | THE ABOVE APPROVED LMI WAS REVISED IN THE MONTH OF FEB.’2022. THE ENVISAGED CHANGES IN LMI ARE | 226474 | MAY PLENASE ACCORD APPROVAL FOR INCORPORATING THE CHANGES AS PER REVISION IN SUBJECT LMI. | 19:44:57 | THE FOLNLOWING CHANGES MARKED IN BOLD HAVE BEEN INCORPORATED AS PER OGN IN NEW LMI DOCUMENT | MARKED IN BOLD | NEW LMI BTL DOC | ATTACHED AS ANNEXURE NEW LMI BTL DOC | 1. PAGE NO. 2 OF 15 INTRODUCTION | 2. PAGE NO. 10 OF 15 REPORTING OF TUBE FAILURE | REPORTING OF TUBE FAILURE | POINT NO. 34 ADDED IN C2 FORM | 3. PAGE NO. 15 OF 15 POINT NO. 34 ADDED IN C2 FORM | 09:05:29 | 10:13:18 | 08:25:48 | 10:28:37 | 12:01:10 | ISSUE NO.1; REVISION NO.1; DATE: MAY 2022 | BOILER TUBE FAILURE | ANALYSIS AND CONTROL | ………………………...……………………....….. | TITLE: BOILER TUBE FAILURE ANALYSIS AND CONTROL HIGH | REV: 1 DATE: MAY’22 | PAGE : 1 OF 15 | 1.0INDEX | 2.0 INTRODUCTION 29 | 3.0 SCOPE 9 | 4.0 REFERENCE DOCUMENT 9 | 5.0 SUPERSEDED DOCUMENT 9 | SPECIFIC INSTRUCTIONS | 6.0 9 | METOLOGY OF | 7.0 IMPLEMENTATION | 8.0 EXCEPTION REPORTING 11 | 10.0 RECORD KEEPING 11 | 11.0 REVIEW 11 | 12.0 REVISION INDEX 12 | 13.0 DISTRIBUTION LIST 13 | 14.0 COMPLIANCE RECORD 14 | FORM C-2 | 15.0 ANNEXURE1 FORM C2 15 | TITLE: BOILER TUBE FALIURE ANALYSIS AND CONTROL | REV: 1 DATE: MAY 22 | PAGE : 2 OF 15 | 2.0INTRODUCTION | BOILER TUBE FAILURES ANALYSIS IS THE FIRST STEP TOWARDS CONTROL OF BOILER TUBE FAILURES. NTPC IN LINE WITH | AND CAUSES SIGNIFICANT FINANCIAL LOSS TO THE COMPANY. INCREASED SIZE OF THE UNITS HAS INCREASED THE LOSS | MULTIPLE FOLD AND THEREFORE THERE IS MORE MANAGEMENT CONCERN TO CONTROL THIS PREVENTABLE LOSS. | BOILER TUBE DAMAGE ACCUMULATION AND EVENTUALLY FINAL FAILURES ARE DUE TO VARIOUS REASONS WHICH ARE | SOMETIMES VERY COMPLEX AND NEED IN H ANALYSIS AND THEREFORE TIME CONSUMING. BOILER TUBE FAILURES | DUE TO BUILD QUALITY DEVIATION FROM ORIGINAL WITH RESPECT TO APPROVED DESIGN DURING ERECTION | EXCURSIONS | CHEMICAL PARAMETER | MISALIGNMENT | SUPPORTS | TUBE | INCOMPLETE FIN WELDING | IMPROPER | IMPROPER PREHEAT AND PWHT DURING ERECTION | TUBES ARE REGULARLY COMING UP EVEN AFTER AVAILABILITY OF | SPECIFIC INFORMATION TO AVOID THEM. | DESIGN FAILURES” OF ATTACHMENTS DUE TO THERMAL TRANSIENTS CAUSING FATIGUE HAVE BECOME NEW AREA OF | CHALLENGE AS CYCLIC LOADING REQUIREMENT OF THE UNIT AS PER GRID DEMAND AND INTRODUCTION OF AGC | FGMO HAS INCREASED SUBSTANTIALLY. IT IS DESIRABLE TO KEEP MS TEMPERATURE VARIATION STANDARD | DEVIATION LESS THAN 3.5. | CHEMICAL PARAMETER DEVIATIONS DURING STARTUP ARE QUITE CRITICAL FROM POINT OF VIEW OF SUPERCRITICAL BOILERS | USING LOT OF STAINLESS STEEL WHICH IS HIGHLY SUSCEPTIBLE FOR STRESS CORROSION CRACKING. EXFOLIATION OF SS TUBE | SCALES DUE TO WIDE TEMPERATURE FLUCTUATIONS AND EXCURSIONS DURING START UP AND SHUT DOWN ARE CRITICAL AREA | OF CONCERN IN SUPERCRITICAL BOILER. THIS CATEGORY HAS BEEN INCREASING IN RECENT YEARS WITH THE INCREASE IN | RAMP UP | DOWN OF THE UNITS IN VIEW OF GRID REQUIREMENT. FREQUENT REVISIONS IN LOAD SCHEDULE | HAS FURTHER AGGRAVATED THE FATIGUE STRESS ON THE MACHINES. BOILER COMPONENTS ARE SIGNIFICANTLY AFFECTED BY | THE THERMAL CYCLES AND THEIR SEVERITY. THERE IS GOOD EVIDENCE THAT INTERLIGAMENT CRACKING ON SUPERHEATER | OUTLET ERS IS EXACERBATED BY SUCH TRANSIENTS AND THE INCREASE IN THE INCIDENCE OF TYPE IV CRACKING. | ATTACHMENT FAILURES IN WATER WALL AND SUPERHEATERS CONNECTORS ARE SHOWING INCREASING TREND IN VIEW OF | HIGH THERMAL TRANSIENTS DURING CYCLIC LOADING THEREFORE COMPREHENSIVE ACTION PLAN FROM DESIGN > | CONTROLLING BTL REDUCES SECONDARY DAMAGES IN THE BOILER DUE TO STEAM WASHING AND OVERHEATING | DOWNSTREAM OF THE FAILURE CAUSED BY THE PRACTICE OF “RUNNING ON” WITH A LEAK TO GET AN OPPORTUNITY FOR A | SUITABLE OUTAGE PERIOD. THIS LMI PROVIDES THE LIST OF ALL GUIDELINES ISSUED BY COS TO CONTROL THE BOILER | TITLE: BOILER TUBE FAILURE ANALYSIS AND CONTROL | REV: 1 DATE: MAY22 | PAGE : 3 OF 15 | WATER LEAKAGE CAUSES LOCATION SAMPLE PHOTO | TOUCHED APPEARANCE | A. WATER WALL THCIK EDGE FRACTURE | CORROSION THICK POOR WATER HIGH STRESS | HIGH ATTACHMENTS | FATIGUE EDGE | BENDS | HOLE | PPHATE AT NEUTRAL AXIS | GENERALLY AT COLD SIDE | CIRCULAR HIDE OUT | BLOW IMPROPER LAY OF TUBE IN WATER WALL | CRACK | ECONOMIZER | OUT UP | CYCLING | HIGH HEAT FLUX AREA | HYDROGEN THICK EDGE CONDENSER LEAK | DAMAGE WINDOW POOR WATER ON HOT SIDE OF WATER | START WALL | NEAR FLOW | DISRUPTIONS | THERMAL THICK EDGE WATER WALL MAXI HEAT FLUX AREA | FATIGUE CRACKS DEPOSITS | POOR OF | SUPERCRITICAL FROM OUT WATER WATER WALL | HIGH | WET TO DRY | CHANGEOVER | THERMAL THICK EDGE FREQUENT START ECO I | L ER NEAR | L POINT | FEED WATER I | FATIGUE CRACK | PIN UP | ECONOMISER HOLE AT | INLET STUB TOE | LOW THICK EDGE RESIDUAL STRESS TUBE BENDS WITH | HIGH STRESS | TEMPERATURE CRACKS AT OF COLD FORMING | CREEP OUTSIDE DEFORMATION IN | SURFACE BENDING | ZIGZAG | IMPROPER WATER STAGNATION | CHEMICAL ROUGH CLEANING ZONE AFTER CLEANING | CLEANING UNDERCUT AND | E.G. | DAMAGE PITS FLUSHING | HORIZONTAL | SLANT | FATIGUE IN THICK EDGE ER AND FEED NEAR ATTACHMENTS | COOLED TEMPERATURE ATTACHMENTS | CIRCUITS DIFFERENCE | PAGE: 4 OF 15 | B WATER WALL THIN EDGE FRACTURE | NEAR SIDE AND | FLY ASH THIN COAL QUARTZ | EROSION EDGE FISH UNBALANCED AIR REAR WALLS | MOUTH FLOW AND EXCESS AIR II PASS | PLUGGED | OUT OF | MISALIGNMENT PASSAGES | FLOW | ALIGNMENT TUBES | ACID THIN EDGE PPHATE HIDE HIGH HEAT FLUX | POOR WATER AREA ON HOT | PPHATE LEAK | SPLIT OUT | HIGH SIDE OF WATER | BLACK WATER WALL | CAUSTIC THIN EDGE POOR WATER HIGH HEAT FLUX | HIGH AREA ON HOT | GAUGING LEAK | CAUSTIC>2PPM SIDE OF WATER | WALL | REDUCING ZONE | FIRE SIDE THIN EDGE FISH SADC MISMATCH | CORROSION MOUTH COAL COMPOSITION HIGH HEAT FLUX | AREA IN BURNER | ZONE | EROSION THIN EDGE | L ER | POOR WATER ECO I | HIGH STUB TUBES | NEAR | ECONOMIZER FROM INSIDE DO FEED WATER I | INLET POINT | FAC | SOOT THIN POOR SOOT BLOWER NEAR SOOT | BLOWER | EROSION MOUTH PROTECTION ESPECIALLY TUBES | PERPENDICULAR TO | SOOT BLOWER OR | OUT OF PLANE | PAGE : 5 OF 15 | HIGHEST HEAT | SHORT GENERALLY LOW DRUM LEVEL | ORIFICE LOCATION LIKE | OVERHEATING EDGE | SOMETIME PLUG GAGE BURNER | S THICK TOP ZONE AND | EDGE GOOSE | NECK AREA FIRE | SIDE TUBE. | PITTING IN PITTING ON POOR WATER AT HORIZONTAL | TUBES AND | COOLED SURFACE OF PRESERVATION COILS | TUBES WATER | COAL THIN DAMAGED BURNERS BURNER TRANSITION | THROAT AND | PARTICLE EDGE TIPS TUBES | EROSION QUAL REGION | FALLING THIN IMPROPER AIR SLOPPING WALL | SLAG EDGE DISTRIBUTION | EROSION | IMPROPER S PANEL | DAMAGE SUPPORT | ACID DEW THIN LOW FLUE GAS EXIT LAST STAGES OF | POINT EDGE TEMP < 120 DEG ECONOMISER | < 120 DEG | CORROSION | 374089 | 17:57:39 | 202317:57:39 | 023 NEGATIVE PHASBE | SEQUENCE ALARMS AT GENERATING STATIONS. O | NO CHANGES ARE ENVISAGED BY COS. ONLY PERIODIC REVIEWING IS DONE AFTER TWO YEARS. NO CHANGES IN THE | DOCUMENT. | उत्तम दौलुई दोलुई उप महाप्रबंधक | UTTAM DOLUI 009601 DY. GENERAL MANAGER | 9434004648 | UDOLUI@NTPC.CO.IN | 17:58:16 | 17:59:14 | APPEARANCE OF NPS ALARM SHOULD BE INTIMATED TO ELECTRICAL. ACCORDINGLY THE | AS PER CNLAUSE 7.1 OF OGN | POINT MAY BE ADDED TO CLAUSE 5.4 IN LMI. | 09:24:48 | ADDED NAS ADVISED. | 10:46:05 | 12:11:47 | THROUGH ME AND I | 10:32:56 | COMPLINED. | 16:28:16 | 10:03:16 | मेड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ा नाग राजा उप महाप्रबंधक | 16:41:09 | 09:31:46 | REVIEWNED THE LMI AND FOUND IN LINE WITH OGN. | MAY PROCESS FURTHER AND APPROVE | 10:17:01 | LMI REVNIEWED AS PER OGN AND FOUND IN ORDER | 18:08:17 | 08:42:06 | PLEASE ANDD REVISION NO. AS DOCUMENT IS CHANGED | 15:52:52 | REVISIONN ADDED. | LMI IS REDRAFTED. | 17:44:02 | ISSUE2N IS TO BE ELIMINATED EVERY WHERE AS REVISION IS DONE | 17:49:03 | COMPILNED. | 18:00:53 | 18:04:11 | 10:05:52 | LMI IS NREVIEWED AND FOUND AS PER OGN. | 18:51:22 | REVIEWNED AND SUBMITTED FOR KIND APPROVAL. | 20:15:33 | 15:40:01 | REVISION:5 | REVISION5 | GENERATOR ROTOR END WINDING | RETAINING RINGS | LMINAME : GENERATOR ROTOR END WINDING | ISSUE NO. 1 REVISION : 5 DATE :OCT 2023 | 6.0 METOLOGY OF IMPLEMENTATION 5 | 7.0 FREQUENCY OF CHECKING AND MEASUREMENTS 5 | 11.0 RECORDS OF REVISION 6 | 12.0 CHECKLIST 7 | FAILURES OF GENERATOR ROTOR RETAINING RINGS HAVE BEEN EXPERIENCED ON | NUMBER OF OCCASIONS. OBJECTIVE IS TO TAKE VARIOUS MEASURES TO AVOID THE | FAILURE DUE TO: | A DUE TO COMBINATION OF STRESS IN COMPONENTS AND EXPOSURE TO AN | INCLUDING PURE WATER. | AGGRESSIVE ENVIRONMENT | B DUE TO FRETTING WHICH IS A WEAR | THE SLIGHT RELATIVE MOVEMENT OF CONTACTING SURFACES. | C CRACKING | TO SAFEGUARD AGAINST THESE | RINGS IN SERVICE: | RELATIVE HUMIDITY INSIDE GENERATOR HAS TO BE CONTROLLED. INSIDE | GENERATOR CASING THE COOLING MEDIA DEW POINT IS TO BE CONTROLLED UNDER | ALL CONDITION OF LOAD OR NO LOAD. THIS CAN BE DONE BY MAINTAINING H2 GAS | DEW POINT TEMPERATURE BELOW 0 DEG C AT FRAME PRESSURE. COLD GAS | TEMPERATURE IS TO BE MAINTAINED ABOVE 20ºC. COLD GAS TEMPERATURE | BEING HIGHER. | RINGS DISMANTLED: | AFTER WRAPPING THE RING | REMOVED RINGS SHOULD BE KEPT IN CONTAINERS | WITH TERYLENE REINFORCED POLYTHENE WRAPPED AROUND. A DESICCANT FOR | MOISTURE ABSORPTION IN SEALED BAG TO BE PLACED INSIDE CONTAINER. ANY | THE DOCUMENT COVERS THE ROTOR RETAINING RINGS FOR GENERATORS OF UNIT – | 3.0 REFERENCE DOCUMENT : | 005. | 2 500MW BHEL GENERATOR O | M MANUAL | 5.0 SPECIAL INSTRUCTIONS TO BE FOLLOWED: | MEASUREMENT | CONTROL. GENERATOR O | MAINTAINING THE COLD GAS TEMPERATURE AND STATOR WATER I | DURING GENERATOR OVERHAUL WHEN ROTOR IS THREADED OUT TWO NDT TEST | ON RETAINING RINGS TO BE CARRIED OUT | I FLUORESCENT DIE PENETRATION TEST: THIS IS THE MOST SENSITIVE | MET AND IS CAPABLE OF DETECTING VERY SMALL CRACKS | II ULTRASONIC TEST: THIS MET WILL DETECT ALL MAJOR DEFECTS | HOWEVER | BE DIFFICULT | TO DETECT CRACKS CLOSE TO SURFACE. | THE MET IS USEFUL BECAUSE IT CAN BE CARRIED OUT WITH END RINGS IN | SITU BUT SHOULD NOT BE RELIED UPON AS A GUARANTEE OF FREEDOM FROM | ALL DEFECTS. | ADVICE | FOR FURTHER DETAILS ON DP AND ULTRASONIC TESTING PROCEDURES | OR THE | MANUFACTURES. | DISMANTLING OF SUCH RETAINING RING IS NOT SUGGESTED BY THE GUIDANCE | 7.0 FREQUENCY OF CHECKING AND MEASUREMENTS: | DURING GENERATOR MAJOR OVERHAULING. | WEBSITE | ENVIRONMENT REPORTS | NDT ON RETAINING RING DURING ELECTRICAL GENERATOR TEST | GENERATOR MAJOR O | THE EXCEPTION | DISPENSATION OF DEVIATIONS: EXCEPTION WILL BE REPORTED | TO EM. | 9.0 RECORD KEEPING: | SHIFT LOGBOOK | GENERATOR TEST FORMAT. | 10.0 REVIEW: | DOCUMENT WILL BE REVIEWED AFTER TWO YEARS BY HOP SIMHADRI. | 11.0 RECORDS OF REVISION: | IFLUORESCENT DIE PENETRATION TEST AND ULTRASONIC TEST DESCRIBED IN | CLAUSE 6.0. | IICHECKLIST ADDED AT CLAUSE 12.0 | M MANUAL FOR COLD GAS | IIIREFERENCE GIVEN TO GENERATOR O | TEMPERATURE CONTROL IN CLAUSE 5.0 | IV500MW BHEL GENERATOR O | M MANUAL ADDED AS REFERENCE | DOCUMENT IN CLAUSE 3.0 | VLMI REVISED AS OGN | 005 REVISED IN JUNE 2020. | NTPC SIMHADRI 7 | 12.0 CHECKLIST: | WEEKLY MONITORING OF H2 DEW POINT TEMPERATURE. | SL NO DATE OF UNIT#1 UNIT#2 UNIT#3 UNIT#4 REMARKS | SAMPLE | 267220 | 202218:08:19 | 18:08:19 | SUBJECT:: REVISION OF LMI | 004 ELECTRICAL TEBSTING | OF GENERATOR ROTOR WINDING INSULATION. O | 004 ELECTRICAL TESTING OF GENERATOR | ROTOR | WINDING INSULATION. | 18:10:58 | PEROIDINC REVIEW | 18:46:36 | REVIEWNED AND MAY BE APPROVED | 19:06:58 | 08:46:50 | 10:48:03 | 11:07:03 | 12:13:58 | DT JULY 2022 | REVISION4 | DATE: JULY 2022 | ELECTRICAL TESTING OF GENERATOR ROTOR | WINDING INSULATION | LMINAME : ELECTRICAL TESTING OF GENERATOR ROTOR | ISSUE NO. 1 REVISION : 4 DATE :JULY 2022 | CID:4667 | CID:4666 | PREPARED BY SR. MANAGER CID:4666EMCID:4667 | CHECKED BY DGM CID:4666EMCID:4667 | CHECKED BY AGM CID:4666EMCID:4667 | REVIEWED BY AGM CID:4666EMCID:4667 I | REVIEWED BY GM CID:4666MAINTCID:4667 | MCID:4667 | REVIEWED BY GMCID:4666O | 4.0 SUPERCEDED DOCUMENT 5 | 7.0 FREQUENCY OF CHECKING AND MEASUREMENTS 7 | DISPENSATION OF 8 | DEVIATION | 10.0 RECORD KEEPING 8 | 11.0 REVIEW 8 | 12.0 RECORDS OF REVISION 8 | ANNEXURE1 9 | ANNEXURE2 10 | THE ELECTRICAL INSULATION USED IN GENERATOR ROTOR WINDINGS HAS TWO | FUNCTIONS. IT PROVIDES THE MAIN INSULATION BETWEEN THE WINDING AND THE | ROTOR BODY AND BETWEEN ADJACENT TURNS IN THE ROTOR WINDING. ꞏ | LOCALIZED DETERIORATION OF THE INSULATION IN SERVICE WILL EVENTUALLY RESULT IN | THE DEVELOPMENT OF UNACCEPTABLY LOW INSULATION RESISTANCE EITHER TO THE | AN EARTH FAULT | ROTOR BODY AN EARTH FAULT OR BETWEEN ADJACENT TURNS IN THE ROTOR WINDINGS | AN INTER-TURN FAULT OR SHORTED TURN | AN INTERTURN FAULT OR SHORTED TURN. | ALTHOUGH GENERATORS CAN OPERATE WITH A SINGLE EARTH FAULT IN THE ROTOR | SHOULD A SECOND EARTH FAULT DEVELOP CATASTROPHIC DAMAGE CAN | THEREFORE | RESULT. IT IS OF GREAT IMPORTANCE | IN DECIDING WHETHER TO CONTINUE | THAT ITS SEVERITY AND POSITION ARE | ACCURATELY ASSESSED. | SHORTED TURNS DEVELOP IN GENERATOR ROTOR WINDINGS WHEN THE INTERTURN | INSULATION BETWEEN ADJACENT TURNS BECOMES DEFECTIVE. IF THE INSULATION | RESISTANCE REDUCES SIGNIFICANTLY | CURRENT IN THE ROTOR WINDING MAY BYPASS | INTERTURN FAULTS WILL BE TO INCREASE THE THERMALLY DEPENDENT VIBRATION OF | WHICH | THE ROTOR AND | OR CAUSE OVERHEATING AT THE POINT OF FAULT | SUBSEQUENTLY COULD RESULT IN A GENERATOR ROTOR EARTH FAULT. | IN TE CASES WHERE THE INTERTURN DEFECT IS OF RELATIVELY HIGH RESISTANCE | AND IS NOT CURRENT CARRYING | SIGNIFICANCE BUT MAY BE INDICATIVE OF LONG TERM DETERIORATION OF THE | INSULATION. | THE AIM OF THIS LMI IS TO PROVIDE A STANDARDIZED APPROACH FOR MONITORING | THE HEALTH OF THE ELECTRICAL INSULATION SYSTEMS OF GENERATOR ROTOR WINDINGS | DURING SERVICE LIFE. THIS WILL ALLOW THE DIRECT COMPARISON OF RESULTS | OBTAINED FROM MANUFACTURERS WORK TESTS AND TESTS UNDERTAKEN DURING | METS WHICH ARE USED IN ASSESSING THE CONDITION OF THE MAIN AND INTER | TURN INSULATION SYSTEMS OF THE ELECTRICAL WINDINGS OF LARGE GENERATOR ROTORS | 4.. | UNIT 1 | 3.0 REFERENCE DOCUNMENT: | A COSISO00OGN | 004 REV NO.: 1 DATE: JUNE 2020 . | B GENERATOR MANUAL O | 5.0 SPECIFIC INSTRUCTION TO BE FOLLOWED: | TABLE 1 GIVES GUIDANCE ON THE USE OF SPECIFIC TEST METS AVAILABLE FOR | DETECTING | LOCATING AND ASSESSING THE SEVERITY OF ROTOR WINDING INSULATION | FAULTS. | ALSO INDICATED ARE THE ROTOR CONDITIONS UNDER WHICH EACH TEST MAY BE | APPLIED AND THE FREQUENCY AT WHICH IT SHOULD BE CARRIED OUT. | 6.0 METOLOGIES OF IMPLEMENTATION | ASSESSMENT OF INTERTURN FAULTS | I MEASUREMENT OF ROTOR WINDING IMPEDANCE | DEVELOPMENT OF A CURRENTCARRYING INTER TURN FAULT REDUCES THE | OVERALL IMPEDANCE OF THE ROTOR WINDING. APPLYING AN EXTERNAL A.C. | VOLTAGE ACROSS THE MULTI CONTACT PINS PERMITS MEASUREMENT OF THE | ROTOR WINDING IMPEDANCE AT STANDSTILL OF THE ROTOR. REFER ANNEXURE 2. | II RECURRENT SURGE OSCILLOGRAPH RSO MET | RSO | IN THIS TEST | FAST RISE TIME PULSES ARE INJECTED INTO THE | LOW VOLTAGE | ROTOR WINDING VIA THE MULTI PIN CONTACT. THE PREFERRED TEST WAVEFORM | IS A REPETITIVE RECTANGULAR PULSE. THE PULSES PROPAGATE THROUGH THE | 195567 | D18 | 202216:23:07 | 16:23:07 | SUBJECT:REVISION OF LMI ON HANDLING OF ELECTROSTATIC B | SENSITIVE DEVICES | GROUNDING REQUIREMENTS O | I003 WAS APPROVED ON 02.06.2022 TO INCLUDE THE FOLLOWING POINTS: | A. OGN ING CHANGED FROM “HANDLING OF ELECTROSTATIC SENSITIVE DEVICES” | GROUNDING REQUIREMENTS" | TO“HANDLING OF ELECTROSTATIC SENSITIVE DEVICES | B. RECORDS TO BE MAINTAINED TABLE CONTENTS REVIEWED | AND FREQUENCY COLUMN ADDED. | C. ANNEXURES DRAFT FORMAT OF RECORDS TO BE MAINTAINED ADDED | TO INCLUDE THE ABOVE CHANGES LMI ON 'HANDLING OF ELECTROSTATIC SENSITIVE DEVICES | GROUNDING REQUIREMENTS' IS BEING REVISED. | I003 AND DRAFT LMI IS ATTACHED FOR REFERENCE. | PUT UP TO COMPETENT AUTHORITY FOR KIND APPROVAL OF THE REVISED LMI. | 17:08:15 | MAY PNLEASE APPROVE. | चौ. िकशोर कुमार अपर महाप्रबंधक | CH KISHORE KUMAR 006106 ADDL. GENERAL MANAGER | CHKISHOREKUMAR@NTPC.CO.IN | 9440918196 | 11:26:09 | 1. PARA N9.0 DOCUMENTS RELATED TO SL NOS 1 | 3 AND 4 MAY BE COLLECTED AND ANNEXED | 2. DETAILS OF VMS PANELS | INCLUDING IMWB | VARIOUS PLCS IN OFFSITE AREAS INCLUDING IMWB MAY BE MENTIONED IN THE | DURING OVERHAULING RESISTIVITY MEASUREMENTS HAVE TO BE DONE AND RECORDS TO | ANNEURE3 FOR WHICH YEARLY | BE MAINTAINED | 18:21:26 | 16:13:13 | AS BUNILD DRAWING OF EARTHING AND GROUNDING SCHEME | LAYOUT FOR MAIN PLANT | I SITE UNDER KNOWLEDGE | AND OFFSITE AREA HAVE BEEN UPLOADED IN C | MANAGEMENT TAB. | FOLLOWING LINK CAN BE USED TO SEE THE DETAILS: | FOLDER.PHP?ID=1143 | HTTP: | 10.0.176.1:7001 | 10:29:45 | 12:58:12 | 17:38:02 | LMI RENVIEWED AND FORWARDED FOR FURTHER REVIEW AND APPROVAL | 17:12:08 | 10:35:01 | APPROVNAL MAY PLEASE BE ACCORDED. | 19:32:04 | 10:37:39 | 12:11:53 | 003 REV NO: 07 | JUNE 2022 | SMPP | NO. LMI | ISSUE NO.: 1 REV: 07 DATE: JUNE 2022 | HANDLING OF ELECTROSTATIC | GROUNDING | 003 REV03 ON | GROUNDING REQUIREMENTS” | “HANDLING OF ELECTROSTATIC SENSITIVE DEVICES | VISAKHAPATNAM | NTPC LTD. SIMHADRI | FOR INTERNAL CIRCULATION ONLY | REV NO: 7 | IMPLEMENTATION BY: ……………………………………………… | DATE: ……………. | 1 ¦ P AG E | NATIONAL THERMAL POWER CORPORATION | HANDLING OF ELECTROSTATIC SENSITIVE DEVICES | LMI NAME: | GROUNDING REQUIREMENTS | LMI NO.: LMI | ISSUE NO. 1 REVISION: 07 DATE: JUNE2022 | PREPARED BY AJEET K RAUSHAN SR MANAGERC | CHECKED BY JAYAMOL RACHEL V AGM C | REVIEWED BY CH KISHORE KUMAR AGMC | REVIEWED BY T.R.RAJAGOPALAN C | REVIEWED BY R K JHA GMO | APPROVED BY G C CHOUKSE HOP SIMHADRI | 2 ¦ P AG E | 5.0 MARKING OF ELECTROSTATIC SENSITIVE DEVICES | 6.0 SPECIAL HANDLING PROCEDURE FOR SITE WORK | 7.0 IN SPECIAL HANDLING PROCEDURE FOR STORES | LABORATORY | WORKSHOP | 8.0 GROUNDING | 9.0 RECORDS TO BE MAINTAINED | 10.0 REFERENCE DOCUMENTS | 11.0 ANNEXURES DRAFT FORMAT OF RECORDS TO BE MAINTAINED | DRAFT FORMAT OF RECORDS TO BE MAINTAINED | 3 ¦ P AG E | 664351 IDATE:09 | 202218:16:37 | 18:16:37 | SUBJECT:REVISED LMI ON THE CONTROL OF PFA AGGLOMERATE EMOISSIONS | THE LMI ON "THE CONTROL OF PFA AGGLOMERATE EMISSIONS" LMI | 011 HAS | BEEN REVISED AS PER REVISED OGN "COSISO00OGN | 011" REV. NO.: 2 OCT. 2022. REVISED | LMI AND OGN IS ATTCAHED. | 664351 | MAY PNLZ BE APPROVED. | 11:26:25 | FOLLOWINNG CHANGES INCORPORATED IN REVISED LMI AS PER REVISED OGN: | 1. CLAUSE 7IIIEPURGING OF FLAKES BY TAKING FANS IN SERVICE REMOVED. | 2. CLAUSE 7IIIE REVISED TO ADD IMPORTED COAL AND DUCT CLEANING. | 3. CLAUSE 7IIIE WATER JET WASHING IN DUCT REMOVED. | ATTACHED AS ANNEXURE. MAY PLEASE BE APPROVED. | ATTACHED DOC "REVISED LMI PFA DEC'22 | REVISED LMI ATTACHED DOC "REVISED LMI PFA DEC'22 | 11:46:05 | SUBMITNTED FOR APPROVAL PLS | 09:46:55 | REVISEDN LMI MAY PLEASE BE APPROVED. | 18:27:23 | 11:38:48 | िगरीश चन्द्र चौकसे मुख्य महाप्रबंधक | GIRISH CHANDRA CHOUKSE 002907 CHIEF GENERAL MANAGER | 11:59:31 | ISSUE NO.2; REVISION NO. 5.00; DATE: DEC’2022 | THE CONTROL OF | PFA | PULVERISED FUEL ASH PFA | AGGLOMERATE EMISSIONS | BUH | 1.0 TITLE OF LMI THE CONTROL OF PFA | DATE ISSUE2; REV.5.00; DEC’2022 | 011 REV 02 OCT’2022 | REF.DOCUMENT OGN | 4.PREPARED BY SIGNATURE: ………………………… | SR. MGR BMD | 6. RECHECKED BY | AGM BMD | 7. REVIEWED BY | 8. REVIEWED BY | 8. APPROVED BY | GIRISH CHANDRA CHOUKSE | 9.DATE OF ISSUE | 10. REVISION INDEX ENCLOSED. | 11.DISTRIBUTION LIST ENCLOSED. | NTPC LMI | TITLE: THE CONTROL OF PFA AGGLOMERATE EMISSIONS REV: | 5.00 DATE: DEC’2022 | PAGE : 2 OF 7 | BLENDED | INDIGENOUS | THE COAL INDIGENOUS | BLENDED USED FOR SIMHADRI PROJECT HAS SULPHUR CONTENT VARYING UPTO | 0.5% AND COMBUSTION OF THIS FUEL PRODUCES SULPHURDIOXIDE AND SULPHURTRIOXIDE VAPOURS AS | PART OF FLUE GASES. WHEREVER THE LOCAL GAS TEMPERATURES FALL BELOW THE ACID DEW POINT IN THE | FLUE GAS DUCT WORK OR CHIMNEY ACID CONDENSATION OCCURS. THE RESULTANT WET ACIDIC FILM | PROVIDES SITES FOR THE CAPTURE OF PARTICULATES PRESENT IN THE FLUE GAS FLOW CAUSING THE FORMATION | OF PULVERIZED FUEL ASH PFA AGGLOMERATES. | FRAGILE READILY DETACH FROM THE FLUE GAS DUCTS WITH | THESE AGGLOMERATES WHICH BECOME HARD | CHANGES IN GAS VELOCITIES OR WITH THERMAL CYCLES AND ARE SUBSEQUENTLY EMITTED FROM THE | CHIMNEY OR DEPOSITED ON THE DUCT FLOOR OR CHIMNEY BASE. AGGLOMERATE FLAKE EMISSIONS WHICH | USUALLY WITHIN ONE KM OF | PRINCIPALLY OCCUR DURING UNIT STARTUP FALL OUT IN THE NEARBY AREA | THE STACK. CONSIDERING THE LAYOUT OF THE SIMHADRI PROJECT WITH ITS VICINITY TO ROAD THIS CAN BE | A SOURCE OF NUISANCE AND CAN CAUSE STRONG OBJECTION FROM LOCALS POPULACE. | THE OBJECTIVE OF THIS LMI IS TO INSTRUCT AND MONITOR THE MEASURES TO BE TAKEN FOR MINIMIZING | THE SCOPE OF THIS LMI IS TO DETAIL THE METS THAT ARE TO BE ADOPTED FOR THE CONTROL OF PFA | AGGLOMERATE EMISSIONS. | 011 REV NO.2 OCT’2022. | 5.0 SUPERCEDED DOCUMENT: | ISSUE NO.1: REVISION NO 4.00; DATE : | APPROVED LMI REF: LMI | JULY | THE FOLLOWING THREE PRONGED APPROACH IS TO BE FOLLOWED TO CONTROL PFA AGGLOMERATE EMISSIONS | A MINIMIZING THE PERIOD FOR WHICH FLUE GAS EXIT TEMPERATURES ARE BELOW ACID DEW POINT | B REDUCING AIR INGRESS INTO FLUE GAS THEREBY MINIMIZING LOCALIZED REDUCTION IN TEMPERATURES. | C CLEANING OF DUCT INTERNALS AND CHIMNEY BOTTOM OF ASH AGGLOMERATES. | TITLE: THE CONTROL OF PFA AGGLOMERATE EMISSIONS | REV: 5.00 DATE: DEC’2022 | PAGE :3 OF 7 | I. MINIMIZING THE PERIOD FOR WHICH FLUE GAS EXIT TEMPERATURES ARE | BELOW ACID DEW POINT | A TAKING SCAPH AND KEEPING SCAPH IN SERVICE AS LONG AS IT IS NECESSARY DURING COLD START | UPS | REGULATING STEAM FLOW TO SCAPH SO AS TO MAINTAIN AVERAGE COLD END TEMPERATURES | AFTER APH ABOVE 70° C. EXCEPTION TO THE SAME TO BE RECORDED | AVERAGE COLD END TEMPERATURES AT EACH APH ABOVE 70°C. EXCEPTION TO THE SAME TO BE | RECORDED. | SHUTDOWNS. | C INSPECTION OF SCAPH FOR LEAKAGES AND ATTENDING THE SAME DURING OVERHAUL | COMPLIANCE FOR THE SAME TO BE RECORDED. | FOR THE SAME TO BE RECORDED. | II. REDUCING AIR INGRESS INTO FLUE GAS THEREBY MINIMIZING LOCALISED | REDUCTION IN TEMPERATURES. | A PREOVERHAUL TESTS TO BE CARRIED OUT TO IDENTIFY THE EXTENT OF AIRHEATER SEAL LEAKAGES. | CLEARANCES AND SUBSEQUENT REPLACEMENT IF | B AIR PREHEATER SEAL INSPECTION FOR DAMAGE | NECESSARY AND SEAL SETTING DURING UNIT OVERHAULS. INSPECTION AND WORK ACTIVITIES TO BE | C IDENTIFICATION OF AIR INGRESSES INTO FLUE GAS DUCT FROM THE MANHOLES | TAPPING | NMEJS IN PREOVERHAUL SURVEY AND ATTENDING THE SAME DURING OVERHAUL. INSPECTION OF | POINTS | FLUE GAS DUCT INTERNALS FROM APH TO CHIMNEY TO THE EXTENT FEASIBLE FOR EROSION AND TAKING | PREVENTIVE PATCH WELDING DURING OVERHAUL. INSPECTION | WORK ACTIVITIES TO BE RECORDED. | D POST OVERHAUL SURVEY TO MONITOR THE EFFECTIVENESS OF SEAL SETTING. | PAGE : 4 OF 7 | III. CLEANING OF DUCT INTERNALS | CHIMNEY BOTTOM OF ASH | AGGLOMERATE | A CLEANING OF DUCT FROM APH TO ESP OF ACCUMULATED ASH DURING OVERHAUL. COMPLIANCE FOR THE | CHIMNEY BOTTOM | B CLEANING OF DUCT WALLS FROM ESP TO CHIMNEY TO THE EXTENT FEASIBLE | AGGLOMERATES DURING OVERHAULS. COMPLIANCE FOR THE SAME TO BE RECORDED. | C EVACUATION OF ECOHOPPERS ON REGULAR BASIS AND TO BE MONITORED ON SHIFT WISE. | OF AHP | >80MG | NM3 | E IF EVIDENCE OF SIGNIFICANT AGGLOMERATE EMISSIONS OBTAINED OR DURING FIRING OF HIGH SUPLHUR | COALS LIKE IN IMPORTED COAL | ADVANTAGE OF PLANT SHUTDOWN TO BE TAKEN TO CLEAN DUCTWORK | WALLS BY MANUAL BRUSHING AND TO REMOVE FLAKES AND DEBRIS FROM THE BOTTOM OF DUCTWORK | PRIOR TO THE RESTART OF THE UNIT FANS. | HENCE IF PRIOR | WHILST AGGLOMERATE FLAKING MOST OFTEN OCCURS WHEN PLANT IS TAKEN OFF LOAD | THESE FLAKES AND DEBRIS ARE TO REMOVED FROM BOTTOM OF DUCT | HISTORY OF FLAKING IS OBSERVED | BEFORE RESTARTING. | 8.0 EXCEPTION REPORTING | EXCEPTION UNIT DATE REMARK | OBSERVATION OF PFA | SCAPH NOT IN SERVICE | DURING COLD STARTUP | AVERAGE COLD END | TEMPERATURES LESS THAN 70 | DEG DURING NORMAL | REV.5.00 DEC'22 | PAGE :5 0F 7 | REVISION INDEX | FOR CHANGES | SL NO. REV. NO. DATE DETAILS APPROVED BY | COAL CHANGES INDICATED | 1. REV 1.00 JUL'06 | REVIEWING AUTHORITY REVISED | DISTRIBUTION LIST REVISED | REPAIR ACTION INDICATED IN PT 6 OF | COMPLIANCE RECORD | 2. REV 2.00 JUL’13 MAIN PAGE REV | REV | LMI APPROVAL DOCUMENTS PAGE | S.NO.2B | SEC 5 | PAGE 2 SEC 5 | SEC 11 | PAGE 4 SEC 11 | 3. REV 3.00 DEC’17 LMI APPROVAL DOCUMENTS S.NO. 2B REV | 5 ADDED | 6DESG. CHANGE; | PAGE2 | CL.5 REV NO. CHANGE; PAGE 6 | 9 DESIGN. CHANGE | ADDED | 4. REV 4.00 JULY’20 III .CLEANING OF DUCT | SECTION 7. III E | SECTION 7. III F | PAGE NO 4 SEC 7.III E | SEC 7.III E | SEC 7.III F | PAGE NO 4 SEC 7.III F | 5. REV 4.00 JULY’22 POINT II. C CORRECTION OF NMEPS TO | NMEJS | 6. REV 5.00 DEC’22 CLAUSE 7.III.E REVISED AND PURGING OF | FLAKES BY TAKING FAN IN SERVICE REMOVED. | CLAUSE 7.III.E REVISED TO ADD IMPORTED | COAL AND DUCT CLEANING | CLAUSE 7.III.F WATER JET WASHING IN | DUCT REMOVED | 268266 | 202211:49:22 | 11:49:22 | SUBJECT:LMI PREVENTION OF DAMAGE TO GENERATORS DUE BTO | MOISTURE IN HYDROGEN O | REF: NTPC SIMHADRI | LMI76 DATE: 12.07.2022 | SUB: REVIEW OF LMIPREVENTION OF DAMAGE TO GENERATORS DUE TO MOISTURE IN HYDROGEN | M CHEM SECTION HAS BEEN REVIEWED AND NO CHANGES | THE FOLLOWING LMI PERTAINING TO O | REVISIONS MADE | SL.NO REMARKS | DETAILS | NEXT REVIEW | SHALL BE IN | PREVENTION OF DAMAGE TO | JULY2024 OR | GENERATORS DUE TO LMI HAS BEEN REVIEWED NO | IF OGN IS | CHANGES INCORPORATED. | REVISED | MOISTURE IN HYDROGEN. | WHICHEVER IS | EARLIER. | 21.07.2020 | REV.4 | AGM TMD | OPRN | GM OPRN | GGM SIMHADRI | 11:27:33 | 09:03:51 | 09:17:16 | UNDERSNIGNED IS NOT THE RIGHT RECIPIENT. | FILE IS FORWARDED TO AGM TMD. | AS PER LIST MENTIONED IN PAGE2 | 16:40:01 | FORWARNDED FOR FURTHER PROCESS PLEASE. | 17:41:28 | AGM | ENMD MAY LIKE TO SEE | 17:54:03 | IF ANY | 13:00:08 | 12:58:54 | 17:36:06 | 16:34:48 | 18:51:49 | 10:46:48 | PREVENTION OF DAMAGE TO GENERATORS DUE TO MOISTURE IN HYDROGEN | REVISION: 05 | ISSUE: 01 | PREVENTION OF DAMAGE TO GENERATORS DUE TO | MOISTURE IN HYDROGEN | SL.NO CONTENTS PAGE NO. | 0.0 CONTENTS 1 | 1.0 INTRODUCTION 2 | 4.0 BASIC TERMS | DEFINITIONS 2 | METOLOGY 24 | 5.0 SPECIFIC INSTRUCTIONS | 6.0 REFERENCE DOCUMENT 5 | 7.0 REVIEW 5 | ANNEXURE I 67 | ANNEXURE II 8 | ANNEXURE III 9 | GRAPH 10 | PAGE 1 OF 10 | HYDROGEN IS USED AS THE COOLING MEDIUM IN SIMHADRI TPS GENERATORS AS ITS HIGH HEAT | TRANSFER COEFFICIENT AND LOW DENSITY RESULT IN VERY GOOD HEAT TRANSFER PROPERTY WITH LOW | WINDAGE | FRICTION LOSSES. HOWEVER | PRESENCE OF MOISTURE MORE THAN A PARTICULAR | PROPORTION OF TOTAL VOLUME IN HYDROGEN GAS IS DETRIMENTAL TO INSULATIONS OF WINDINGS AND | ROTOR END RETAINING RINGS. ANY CONDENSATION OF MOISTURE MAY RESULT IN ELECTRICAL FLASHOVERS | STRESS CORROSION CRACKING OF AUSTENITIC ROTOR RETAINING RINGS | PARTICULARLY ON END WINDINGS | AND APPEARANCE OF ROTOR EARTH FAULTS. | REVISION: 04 | 009 ISSUE: 01 | THESE GUIDELINES ARE APPLICABLE TO SIMHADRI 500MW GENERATORS. THE SCOPE OF THESE | 4.0 BASIC TERMS AND DEFINITIONS: | BASIC TERMS | DEFINITIONS ARE GIVEN IN ANNEXURE I | 5.0 SPECIFIC INSTRUCTIONS TO BE FOLLOWED : | SL NO ACTIVITY RESPONSIBILIT | 5.1 OPERATING LIMITS FOR COLD GAS TEMPERATURE ARE SET IN SUCH A WAY SCE | UNIT | THAT AN EXTREME POSSIBLE CONDITION OF LOW TEMPERATURE OF COLD GAS CONTROL | SHALL NOT RESULT IN CONDENSATION OF MOISTURE. THIS IS ACHIEVED ENGINEER | EITHER BY REGULATING COOLING WATER FLOW THROUGH THE GAS COOLERS OR | BY DECREASING DEW POINT OF GAS BY REDUCING THE QUANTITY OF | MOISTURE IN THE GAS ITSELF. NORMAL OPERATING COLD GAS TEMPERATURE | IS 37 OC WITH A MAXIMUM OF 55 OC. HIGH ALARM IS AT 55OC AND VERY | HIGH ALARM IS AT 60OC. GENERATOR PROTECTION IS GIVEN ABOVE 60OC . IT | IS TO BE ENSURED THAT THE DEW POINT OF THE GASVAPOR IN THE CASING | SHALL BE AT LEAST 20OC LOWER THAN THE LOWEST COLD GAS TEMPERATURE | AND COLD GAS TEMPERATURE LIMITS ARE MAINTAINED. | PAGE 2 OF 10 | 5.2 IT IS NECESSARY TO MAINTAIN A TEMPERATURE DIFFERENTIAL BETWEEN COLD SCE | PRIMARY WATER TEMPERATURE AND COLD GAS TEMPERATURE WITH PRIMARY CONTROL | IN THE GAS | WATER TEMPERATURE ON HIGHER SIDE SO THAT MOISTURE | DOES NOT CONDENSE ON ANY SOLID SURFACES SUCH AS STATOR WINDING | COOLING WATER ES | END WINDINGS | WINDING CONNECTIONS. NORMAL | OPERATING DIFFERENTIAL BETWEEN COLD PRIMARY WATER TEMPERATURE AND | COLD GAS TEMPERATURE SHOULD BE MORE THAN 50C AND LOW ALARM IS AT | 30C AND VERY LOW ALARM IS AT 10C. | 5.3 DRIER UNITS HELP IN BRINGING DOWN THE MOISTURE LEVEL IN CASING SCE | HYDROGEN. THESE DRIERS CAN BE PUT INTO SERVICE ONLY WHEN MACHINE CONTROL | IS AT 3000 RPM AND COOLING FAN DIFFERENTIAL FORCES THE HYDROGEN ENGINEER | THROUGH THE DRIER. IT IS THEREFORE | IMPORTANT TO MAINTAIN HYDROGEN | PRESSURE IN THE CASING DURING SHUT DOWN AND BOTH VAPOR EXTRACTORS | OF SEAL OIL SYSTEM SHALL BE KEPT RUNNING SO THAT THE CHANCE OF | MOISTURE TRANSFER FROM SEAL OIL IS MINIMIZED. | 5.4 H2 DRIERS PROVIDED ARE REFRIGERATION TYPE. THE MOISTURE IN THE SCE | HYDROGEN CONDENSES THROUGH COOLING AND CONVERTS IN WATER FORM IN CONTROL | CONDENSATE CHAMBER. IT IS TO BE ENSURED THAT ALL THE MOISTURE IS ENGINEER | REMOVED BY PROPER DRAINING WITHIN 2 TO 3 DAYS AFTER CHECKING | MOISTURE LEVEL THROUGH LOOKING GLASS WINDOW. IT SHOULD BE ENSURED | THAT BOTH THE DRAIN VALVES ARE CLOSED PROPERLY AFTER REMOVAL OF | WATER AND ONLY WATER IS DRAINED OUT | 5.5 REGULAR MONITORING IS REQUIRED TO BE DONE OF CASING DRAINS LLDS | LLDS | SCE | ALTHOUGH AN ALARM IS PROVIDED WHEN THE LEVEL IN "LLD" HAS BUILT UP. CONTROL | LLDS SHOULD BE CHECKED AT LEAST ONCE IN EVERY SHIFT AND RECORDED. IF ENGINEER | WATER IS PRESENT AND IT IS CONTINUOUS THE UNIT SHOULD BE DE | THE CAUSE OF WATER LEAKAGE IDENTIFIED AND ATTENDED. | ENERGIZED | DEW SHIFT | 5.6 BEFORE ENERGIZING THE MACHINE AFTER A PROLONGED SHUT DOWN | THE MACHINE SHALL NOT BE ENERGIZED SCE | BELOW COLD GAS TEMPERATURE | THE MOISTURE LEVEL SHALL BE BROUGHT DOWN TO REQUIRED LEVEL BY CONTROL | PUTTING DRIERS IN SERVICE. THE SPECIFIC VALUE OF DEW POINT IS TO BE ENGINEER | RECORDED AND CLEARANCE FOR EXCITING THE GENERATOR IS TO BE OBTAINED | PAGE 3 OF 10 | 326144 | 12:46:28 | 202212:46:28 | ORT MEETING | ORT | 021 REV. NO.: 3 JULY 2022 | FOLLOWING ARE THE CHAGES AS PER CC OS : | VII | A SOP ADDED IN POINT 2 | B TLA ADDED IN 2 | XVIII | C CLAUSE 6.1.2 REVISED FOR RE GROUP ORT. | D CHANGES REG. PEM MONITORING AND DISCUSSION DONE IN POINTS 6.2.5.V | 6.2.6XIII | XIII | XXVI | 6.2.8.XXVI | XII | 6.2.7.XXVII | 6.3.7.XII | XXVII | E CLAUSE 6.4.5 “HARD COPIES TO BE SEND TO” CHANGED TO “COPIES TO BE MAILED | TO”. | F RGMO ADDED IN CLAUSE 6.3.7.1 | G POINT 6.2.7.XX ADDED REGARDING SHUTDOWN OPPORTUNITY JOBS COMPLIANCE. | XVII | H POINT 6.3.7 XVII ALSO UPDATED REG. MAIN PLANT | CER TEMPERATURE DEVIATIONS | CYBER | OFFSITE CCR | SECURITY READINESS AND INCIDENTS | I POINT 6.3.7 XVIII ALSO UPDATED REG. ELECTRICAL SYSTEMS. J ANNEXURE2 ADDED FOR RE GROUP ORT FORMAT | BUH IS THE APPROVING AUTHORITY. | SUBMITTED FOR FOR KIND APPROVAL . | SUBMITTED FOR APPROVAL PLS. | 12:51:53 | REVIEWED AND FOUND IN LINE WITH OGN | आ ई ए अप | 19:18:01 | प अ ए | 19:10:21 | 12:42:52 | ISSUE NO.1 REVISION NO.3 JULY 2022 | EOFFICE REFERENCE NO: | DATE: 02082022 | 021 REV. NO.: 3 | SIMHADRI SUPER THERMAL POWER | LMI NO : LMI | ISSUE NO: 1 REVISION: 3 DATE: 02.08.2022 | PREPARED BY SUBIR DEBNATH SR.MGR | REVIEWED BY I L REDDY | REVIEWED BY R K JHA GM O | MEETING | SL NO CONTENTS PAGE NO | 2.0 PURPOSE 1 | 3.0 SUPERSEDED DOCUMENTS 2 | 4.0 SCOPE 2 | 5.0 RECORDS OF REVISIONS 2 | 6.0 PROCESS 2 | 6.1 REQUIREMENTS | RESPONSIBILITIES 2 | 6.2 PREPARATION FOR ORT MEETING 4 | 6.3 ORT MEETING 8 | 6.4 REPORT OF ORT MEETING 11 | 6.5 POST ORT ACTIONS AND FOLLOW UP 12 | 6.6 RECORDS 13 | 7.0 REVIEW 13 | ANNEXURE 1PROCESS FLOWCHART FOR ORT MEETING 14 | ANNEXURE 2 RE GROUP ORT FORMAT 15 | 2.0 PURPOSE | REVIEW TEAM ORT OF POWER STATION. | OBJECTIVES OF ORT MEETINGS ARE: | IDENTIFYING SHORTFALLS IN PERFORMANCE PARAMETERS | UNIT CAPABILITY AND CORRECTIVE | ACTION THEREOF. | II TO FINALIZE MEASURES FOR MAXIMIZATION OF GENERATION AS PER REQUIREMENT OF THE | GRID. | III TO IDENTIFY MAJOR CONSTRAINTS | M ISSUES INCLUDING ISSUES | DEVIATIONS AND O | REFERRED TO CC AND FINALIZE ACTION PLANS FOR IMPROVEMENTS | IV TO REVIEW FORCED OUTAGES AND PARTIAL LOADING DETAILS AND FINALIZATION OF | MEASURES FOR REDUCTION. | V TO REVIEW THE MEASURES TAKEN FOR O | M COST REDUCTION | OPTIMIZATION | VI TO IDENTIFY AND ANALYZE THE EFFICIENCY GAPS OF THE UNITS | SYSTEMS AND FINALIZE | SO AS TO ACHIEVE THE TARGETED HEAT RATE. | MEASURES FOR IMPROVEMENT | PROCEDURES AND TECHNICAL | VII TO VERIFY COMPLIANCE OF VARIOUS TECHNICAL SYSTEMS | COMPLIANCE DOCUMENTS ODS | VIII TO VERIFY COMPLIANCE OF SAFETY SYSTEM INCLUDING FIRE FIGHTING SYSTEM. | X TO REVIEW STATUS OF RENOVATION | MODERNIZATION IN THE STATION AS APPLICABLE. | XI TO REVIEW O | XII TO REVIEW THE STEPS TAKEN FOR CONSERVATION OF ENERGY AND OTHER RESOURCES | INCLUDING STATUS OF EC BUDGET ACTIVITIES | UTILIZATION. | RESULTS ACHIEVED | XIII TO REVIEW COMPLIANCE OF STATUTORY REQUIREMENTS. | XIV TO REVIEW ACTION PLANS OF ROPR. | XV TO REVIEW THE STATUS OF ACTION PLANS ARISING OUT OF VARIOUS AUDITS TECHNICAL | INTERNAL TECHNICAL COMPLIANCE AUDIT BY POWER | AUDIT BY CORPORATE OS | EXTERNAL TECHNICAL COMPLIANCE AUDIT BY REGION | SAFETY AUDIT | ENERGY AUDITS ETC.. | XVI TO REVIEW STATUS OF PENDING PG TESTS | IF ANY. | REPORTS | XVII TO REVIEW THE ACTION PLANS ARISING OUT OF VARIOUS REVIEWS | INVESTIGATIONS | TLA ETC | XVIII TO REVIEW IT ENABLED SYSTEMS RELATED ISSUES SAP | PI SYSTEM | INCLUDING COMPLIANCE. | PAGE NO1 | 021 REV. NO. : 0 AUGUST 2005 | 021 REV. NO.: 1 DATE: SEPTEMBER 2015 | REV. NO. 2 APR 2020 | 021REV. NO.: 2 MAY 2022 | 5.0 RECORDS OF REVISON | CER TEMPERATURE | CYBER SECURITY READINESS AND INCIDENTS | I POINT 6.3.7 XVIII ALSO UPDATED REG. ELECTRICAL SYSTEMS. | J ANNEXURE2 ADDED FOR RE GROUP ORT FORMAT | 6.0 PROCESS | 6.1 REQUIREMENTS AND RESPONSIBILITIES | 6.1.1 THE ORT MEETINGS OF POWER STATION WOULD BE ORGANIZED BY OF | REGIONAL OS AT POWER STATION OR THROUGH VC IN RESPECT OF ALL POWER STATIONS IN THE | ORT COORDINATOR | REGION AND COORDINATED BY NOMINATED EXECUTIVE ORT COORDINATOROF REGIONAL | OS. CORPORATE OS STATION COORDINATOR SHALL ATTEND THE ORT AT LEAST TWICE IN A | THE FIRST BEING PREFERABLY IN THE FIRST HALF OF THE YEAR AND THE SECOND IN THE | SECOND HALF OF THE YEAR. | THE ORT MEETINGS WOULD BE HELD ON OR BEFORE 7TH WORKING DAY OF THE MONTH. THE | VENUE OF THE MEETING WOULD NECESSARILY BE THE POWER STATION. THE DATES WOULD BE | FINALIZED BY OF REGIONAL OS IN CONSULTATION WITH THE OF THE POWER | STATION. THE ORT MEETINGS WOULD BE HELD IN TWO STAGES: | PAGE NO2 | I PREORT DISCUSSIONS – VISIT OF ORT TEAM TO STATION AND THEIR | S OF VARIOUS DISCIPLINES IN THE | DISCUSSIONS WITH CONCERNED ENGINEERS | POWER STATION – SPANNING NORMALLY 1 2 DAYS. THE MEMBERS OF PRE ORT | TEAM SHOULD BE AVAILABLE THROUGH VC ON THE DAY OF ORT IF ORT IS | CONDUCTED THROUGH VC. | II ORT MEETING –MEETING CHAIRED BY OF STATION AND PARTICIPATED BY | ALL CONCERNED S OF THE POWER STATION AND ORT | COORDINATOR FROM REGION. CORPORATE OS STATION COORDINATOR WILL ATTEND THE | ORT MEETING AT LEAST TWICE IN A YEAR. | NOTE: PLEASE SEE PROCESS FLOWCHART FOR ORT MEETING ATTACHED AS ANNEXURE IN THIS | 6.1.2 FOR SOLAR PLANTS INSTALLED IN THE EXISTING COAL STATIONS THE RELATED ISSUES WILL | BE DISCUSSED EVERY MONTH ALONG WITH THE ORT OF THE ASSOCIATED STATION. | 6.1.3 THE ORT MEETINGS WOULD NECESSARILY BE CHAIRED BY OF THE POWER | IF OF | STATION DURING THE FULL MEETING. IN CASE OF EMERGENT SITUATION | HE WILL OBTAIN VERBAL APPROVAL OF | POWER STATION IS NOT IN A POSITION TO ATTEND | REGION | M OF THE STATION WOULD CHAIR THE | RED REGION AND IN THAT CASE OF O | ORT MEETING. | 6.1.4 THE FOLLOWING EXECUTIVES WILL PARTICIPATE IN THE ORT MEETING. | A. POWER STATION: | I. OF POWER STATION IN CHAIR | II. OF O | M OF POWER STATION | IV. ALL S OF O | V. OF HR | VI. OF FINANCE | VII. OF SAFETY | VIII. OF ENVIRONMENT AND ASH UTILIZATION | IX. OF IT | X. OF TECHNICAL SERVICES | XII. OF C | XIII. OF BE | XIV. OF R | XV. SHIFT CHARGE ENGINEER. | PAGE NO3 | XVI. ANY OTHER | EXECUTIVE AS PER REQUIREMENT. | B. REGIONAL OFFICE | I. REGIONAL OS ORT COORDINATOR | II. ONE ADDITIONAL EXECUTIVE FROM REGION OS AS PER REQUIREMENT | C. CORPORATE CENTRE | STATION COORDINATOR OF CORPORATE OS – AT LEAST TWICE IN A YEAR. | FOR CONDUCTING ORT MEETINGS. | 6.1.6 THE FLOW OF INFORMATION THE ORT PROCESS IS ENVISAGED THROUGH DIFFERENT | SYSTEMS DEVELOPED IN SAP | IT ENABLED SYSTEMS. AT THE STATION | NECESSARY | IT ENABLED SYSTEMS USED FOR ORT SHALL | AUTHORIZATIONS FOR DIFFERENT SAP | THE AUTHORIZATIONS SHALL BE | BE CONTROLLED BY OF O | M. IN REGION | CONTROLLED BY OF OS. IN CORPORATE LEVEL THE AUTHORIZATIONS SHALL BE | IT ENABLED | 6.1.7 ALL TE ASSOCIATED WITH THE ORT PROCESS SHALL USE THE SAP | PROCESS AS PER THEIR RESPECTIVE ROLES IN THE ORT PROCESS. ALL CONCERNED SHALL | STRIVE TO KEEP THE INFORMATION RELATING TO THEIR RESPECTIVE ROLE ACCURATE AND UPTO | AS THE INFORMATION REQUIRED FOR VARIOUS REVIEWS AND DURING | DATE IN SAP | DIFFERENT STAGES OF ORT PROCESS | WILL BE RETRIEVED FROM SAP ONLY. | 6.2 PREPARATION OF ORT MEETING | 6.2.1 EACH SECTIONS IN STATION SHALL FORWARD THEIR RESPECTIVE FILLED UP | UPDATED ORT | ALL S | DAY OF THE MONTH. | ROPR | STATUS OF NOTIFICATIONS UNDER ORT | TC AS | TECH AUDIT | TRIP ANALYSIS | AND WHEN THERE IS A CHANGE IN STATUS. | SHALL SEND THE DOSSIER CONTAINING VARIOUS | PAGE NO4 | 641558 | 202217:17:02 | SUBJECT:REVIEW OF LMI “GUIDE LINES FOR CARRYING OUT SAFE | 032 O | DATE: 01.12.2022 | CLIMBERS INSIDE BOILER” WITH REF NO: LMI | 032 | THE ABOVE APPROVED LMI WAS REVISED IN MONTH OF AUG ’2022. THE ENVISAGED CHANGES IN LMI ARE | 053. | THE SUBNJECT LMI HAS BEEN REVISED AS PER CHANGES ENVISAGED IN COSISO00OGN | 053 | THE CHANGES ARE INCORPORATED IN LMI DOC WITH REF NO: LMI | ISSUE NO.1; REVISION NO. 02; DATE: DEC’2022. | CA MAY PLEASE ACCORD APPROVAL FOR THIS REVISED VERSION OF LMI. | CHANGENS INCORPORATED IN REVISED LMI IN FOLLOWING CLAUSES: | 1. CLAUSE 7 A 2 | 2. CLAUSE 7 B 2 | 3. CLAUSE 7 C 2 | 4. CLAUSE 7 E 3 | THE ABOVE CHANGES HAVE BEEN HIGHLIGHTED IN ATTACHED DOCUMENT "NEW LMI DOC" | SUBMITTED FOR APPROVAL | 08:41:50 | िचप्पासत्य नारायण अपर महाप्रबंधक | CHIPPA SATYA NARAYANA 031083 ADDL. GENERAL MANAGER | CSNARAYANA@NTPC.CO.IN | 9491876071 | 15:32:05 | 15:50:13 | 17:29:25 | 18:57:12 | 17:19:15 | 15:40:31 | 22:47:11 | ISSUE NO.1; REVISION NO. 02; DATE: DEC’2022 | GUIDELINES FOR CARRYING OUT SAFE | BOILER | GUIDELINES FOR CARRYING OUT | CLIMBERS INSIDE BOILER | DATE ISSUE1; REV: 02; DEC’2022 | REV 0 | 4.PREPARED BY : SR. MANAGER SIGNATURE | AGM SAFETY SIGNATURE | GM MTC SIGNATURE | MTC | CLIMBERS INSIDE BOILER REV 02; DATE: DEC’2022 | PAGE : 1 OF 13 | 7.0 METOLOGY OF MPLEMENTATION | 9.0 RECORD KEEPING 7 | 10.0 REVIEW 7 | 11.0 REVISION INDEX 8 | 12.0 DISTRIBUTION LIST 9 | 13.0 COMPLIANCE RECORD 10 | 14.0 ANNEXURE A 11 | TRAINING RECORD | 15.0 ANNEXURE B 1213 | PROTOCOL FOR SKYCLIMBER SAFETY | CLIMBERS INSIDE BOILER REV: 02; DATE: DEC’2022 | PAGE : 2 OF 13 | SKY CLIMBERS ARE SUSPENDED ACCESS PLATFORMS ESSENTIAL FOR INSPECTION AND REPAIR OF PRESSURE | SAFETY IS | TO 75M APPROX. HEIGHT INSIDE BOILER | APPROX. | FALL FROM HEIGHT IS MAJOR RISK INVOLVED. HENCE | A KEY ASPECT WHILE USING THE SKY CLIMBERS. IT IS NECESSARY THAT EACH AND EVERY PERSON WHO | INTENDS TO UTILIZE THE SKY CLIMBER FAMILIARIZE HIMSELF ABOUT THE PROPER AND SAFE METS | RELATING TO USE OF SKY CLIMBERS ALONG WITH THEIR FUNCTIONS AND LIMITATIONS. | SPECIFIC GUIDELINES. | THE SCOPE OF THIS LMI IS TO DETAIL THE CHECKS TO BE ADOPTED WHILE USING SKY CLIMBERS | TRAINING TO BE IMPARTED TO THE PERSONNEL INVOLVED | AND RECORDS TO BE MAINTAINED. | CIRCULATED BY | 053 REV.0 | ISSUE1; REV: 0.00; JAN’2020 | THE OBJECTIVE OF THE LMI IS SOUGHT TO BE ACHIEVED THROUGH FOLLOWING ACTIONS: | I BY CARRYING OUT SPECIFIC CHECKS AND INSTRUCTIONS AT DIFFERENT STAGES OF USING SKY | CLIMBER I.E. BEFORE SKY CLIMBER ASSEMBLY | BEFORE | EMERGENCY | 984095 | D30 | 202316:45:00 | 16:45:00 | SUBJECT:REVIEW OF LMI “GUIDELINES FOR CARRYING OUT SAFEB | ERECTION OF SCAFFOLDING INSIDE BOILER” O | DATE: 30.03.2023 | SUBJECT: REVIEW OF LMI “GUIDELINES FOR CARRYING OUT SAFE ERECTION OF | SCAFFOLDING INSIDE BOILER” | 046 | THE ABOVE APPROVED LMI WAS PREPARED BASED ON REFERENCE DOCUMENT " COSISO00 | 046" CIRCULATED BY CCOS. THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER | DETAILS AT REVISION INDEX OF LMI. | THE CHANNGES HAVE BEEN INCORPORATED IN THE LMI "GUIDELINES FOR CARRYING OUT SAFE ERECTION OF SCAFFOLDING | 046". | INSIDE BOILER" AS PER CHANGES MENTIONED IN THE REFERENCE DOCUMENT " COSISO00OGN | COMPETENT AUTHORITY MAY PLEASE ACCORD APPROVAL FOR THIS REVISED LMI WITH REVISION NO1 OF DOCUMENT NO | 17:06:19 | FOLLOWINNG CHANGES INCORPORATED IN REVISED LMI ATTACHED AS ANNEXURE "NEW LMI": | 12 ADDED. | 1. CLAUSE 7 A POINTS 10 | 13 ADDED | 2. CLAUSE 7 C PONIS 10 | 3. CLAUSE 7 F POINTS 9 | 10 ADDED | 4. CHANGES INCORPORATED IN ANNEXURED AS PER OGN | 10:02:34 | 10:36:46 | 11:12:15 | 11:15:55 | 11:29:49 | 19:28:24 | FORWARNDED FOR APPROVAL PLEASE | 20:23:19 | 17:26:50 | ISSUE NO.1; REVISION NO. 1.00; DATE: MAR’2023 | ERECTION OF SCAFFOLDING INSIDE | 1.0 TITLE OF LMI SAFE ERECTION OF | SCAFFOLDING INSIDE BOILER | DATE ISSUE1; REV: 1; MAR’2023 | TITLE: GUIDELINES FOR CARRYING OUT SAFE ERECTION OF | SCAFFOLDING INSIDE BOILER REV: 1 DATE: MAR’23 | PAGE : 1 OF 14 | 7.0 METOLOGY OF IMPLEMENTATION | 15.0 ANNEXURE B 12 | PROTOCOL FOR USE OF SCAFFOLDING | 16.0 ANNEXURE C 13 | SCAFFOLDING REGISTER | INSPECTION RECORD | 17.0 ANNEXURE D 14 | PAGE : 2 OF 14 | DIFFERENT TYPES OF SCAFFOLDING ARE BEING REGULARLY USED FOR INSPECTION AND REPAIR OF BOILER | PRESSURE PARTS. SAFETY IS THE MOST IMPORTANT ASPECT WHILE USING THE SCAFFOLDING SYSTEM | BREAKDOWNS | INSIDE BOILER DURING OVERHAULS | THAT EACH PERSON WHO INTENDS TO UTILIZE THE SCAFFOLDING SYSTEM TAKE THE TIME TO LEARN THE | FAMILIARIZING WITH THE FUNCTIONS AND LIMITATIONS OF THE SCAFFOLDING SYSTEM. | THE OBJECTIVE OF THIS LMI IS TO IMPROVE THE SAFETY OF SCAFFOLDING ERECTED INSIDE BOILER BY | FOLLOWING SPECIFIC GUIDELINES. | THE SCOPE OF THIS LMI IS TO DETAIL THE PRACTICES TO BE FOLLOWED WHILE USING SCAFFOLD | WATER WALL OR | PLATEN SH | ROOF TUBES FOR | ANY HANGING COILS IN BOILER FURNACE | GOOSE NECK AREA OR SECOND PASS | INSPECTION OR ANY OTHER JOB REQUIRING ACCESS AT HEIGHT. | 046 REV.1 | A BY CARRYING OUT SPECIFIC CHECKS AND INSTRUCTIONS AT DIFFERENT STAGES OF USING | SCAFFOLDING INSIDE BOILER I.E. | BEFORE USING THE PLATFORMS | DURING ERECTION | WHILE USING THE PLATFORMS | DURING DISMANTLING ETC. | 588412 | 202417:26:32 | 17:26:32 | OF GENERATOR EXCITATION CONTROL SYSTEMS O | 010 | EXCITATION CONTROL SYSTEMS | HAS BEEN REVIEWED BY COS. | RECORDS OF REVISION: NIL | OCT 2024 | REV:00 | 18:11:53 | NO CHANGES ENVISAGED | PERIODINC REVIEW | 19:15:56 | 19:09:30 | 10:01:11 | 15:49:22 | GENERATOR EXCITATION CONTROL SYSTEMS | 010 REV:00 | GENERATOR EXCITATION CONTROL | 010 REV:00 AUG 22 | NAME: SUMIT KUMAR VERMA | NAME: T VIJAY KRISHNA | AGM EMI | 8 REVIEWED BY NAME: P K JENA | 2.0 SUPERSEDED DOCUMENTS 4 | 3.0 DETAILS OF REVISION 4 | 4.1 METOLOGY OF 4 | FUNCTIONAL CHECKS | 4.3 STATIC TESTS 5 | 4.4 DYNAMIC TESTS 6 | 5.0 FREQUENCY OF CHECKING 7 | 7.0 EXCEPTION REPORTING AND 7 | 8.0 REVIEW 7 | 9.0 CHECKLIST 816 | A FULLY FUNCTIONAL | AVR | AUTOMATIC VOLTAGE REGULATOR SYSTEM AVR IS NECESSARY TO ALLOW SAFE | FLEXIBLE | WITHIN SPECIFIC LIMITS AT ANY STEADY LOAD; TO QUICKLY RESTORE THE STATOR VOLTAGE FOLLOWING ANY | SUDDEN CHANGE IN UNIT LOADING OR SYSTEM FAULT | AND TO ASSIST IN MAINTAINING THE STABILITY OF | THE GRID | ENSURE THE RELIABILITY OF AVR SYSTEM PERFORMANCE AND TO PROVE COMPLIANCE WITH GRID CODE | REQUIREMENTS. | 4.1 METOLOGY OF IMPLEMENTATION | SINCE BOTH ARE INTEGRAL PART OF THE GENERATOR EXCITATION CONTROL | EXCITATION CONTROL SYSTEM | 1. PHYSICAL INSPECTION OF ALL COMPONENTS | CABLING | TERMINATIONS | AND RELAY CONTACTS. | TRIP | CLOSE | 2. FUNCTIONAL CHECKING CLOSE | TRIP OF FIELD CIRCUIT BREAKER | 3. INSULATION TESTS. | 5. AVR CHANNEL CHANGEOVER AFTER VOLTAGE BUILD UP AND AVR TROUBLE TO GRP TRIP SIGNAL | NOT LESS THAN THREE MONTHS | ISOLATED ON OPPORTUNITY NOT LESS THAN THREE MONTHS | 4.3 STATIC TESTS | STATIC TESTING INCLUDES THE FOLLOWING AND TO BE CARRIED OUT WHEN GENERATOR IS OFFLINE | 1. OBTAINING THE CHARACTERISTICS OF THE CONTROL STAGES OF THE ECS – BOTH AUTOMATIC | CHANNELS BY SECONDARY INJECTION AND OPTIMIZING THESE RESULTS COMPARED TO THE DESIRED | CHARACTERISTICS. | 2. ENSURING THAT ALL THE ECS PROTECTION AND MONITORING DEVICES ARE FUNCTIONAL AND SET. | 3. VERIFICATION OF TIGHTNESS OF EACH CONTROL | CONNECTORS TERMINATION TO | POWER CABLE | CONTROL TRANSFORMERS AND TBS. | ELECTRONIC MODULES | TRANSDUCERS | 4. PMG FUSE AND CONTROL FUSE BASES SHOULD BE SECURED PROPERLY AND CHECKED FOR TERMINAL | LOOSENESS. PMG FUSES SHALL BE REPLACED IN EVERY EIGHT YEARS. | 5. SEALING OF PANEL | DOOR | SPARE CABLE GLANDS. | 6. ELECTRONIC MODULES ARE TO BE INSPECTED FOR DUST BUILDUP | ANY HEATING MARKS ON | COMPONENTS | PARAMETER SETTING AS PER OEM MANUAL | PROPER JUMPER SETTING | INSTRUCTION. | CUBICLE FILTER CLEANING IS TO BE DONE. | 7. INSPECTION AND TESTING OF POWER THYRISTORS AND ASSOCIATED ELECTRONIC CIRCUITRY. | 8. ENSURING ELECTRONIC EARTHING CONTINUITY AND PROPER GROUNDING OF ELECTRONIC MODULES. | 9. CHECKING OF INSULATION RESISTANCE VALUE OF AVR TROUBLE TO GRP TRIP CONTROL CABLES AND | POWER CABLES | BUS DUCT. PHYSICAL INSPECTION OF CABLE ROUTING NEAR EXCITER FOR ANY | DAMAGE. | 10. CHECKING OF AUXILIARY POWER SUPPLY CHANGEOVER SCHEME FOR CONTROL SUPPLY TO ELECTRONIC | MODULE AND COOLING FANS OF THYRISTOR BRIDGE. | 11. CHECKING OF THYRISTOR COOLING BLOWING MOTOR VIBRATIONS AND CONDITIONS. POWER SUPPLY | SOURCES COOLING FAN BLOWERS SHALL BE CHECKED FOR PROPER TIGHTNESS OF TERMINATIONS | CABLE CONDITION | FUSE HEALTHINESS. | 12. TESTING OF CONTROL AND INSTRUMENT TRANSFORMERS OF AVR PANEL. | 13. ALL JUMPER CONNECTIONS SHOULD BE CHECKED AS PER FACTORY TEST REPORT. | 14. LIST OF PARAMETERS FOR SEPARATE FUNCTIONAL GROUPS WOULD BE CHECKED AND ENSURED | AS PER FACTORY TEST REPORT. | 15. ALL DC AND AC SUPPLY INPUTS TO DAVR WOULD BE CHECKED. | 16. OUTPUT OF ALL TRANSFORMERS WOULD BE CHECKED. | IS TO BE PREPARED. | 18. CALIBRATION OF PARAMETER – UG: INJECT 3 PHASE VOLTAGE TO THE PT INPUT TERMINAL OF BOTH | CHANNELS OF DAVR AND MEASURE THE CORRESPONDING VOLTAGE LEVELS AT DAVR REF: | ANNEXUREI.. | 19. CALIBRATION OF PARAMETER – IG: INJECT 3 PHASE CURRENT TO THE CT INPUT TERMINAL OF BOTH | CHANNELS OF DAVR AND MEASURE THE CORRESPONDING VOLTAGE LEVELS AT DAVR. CHECK THE | EFFECTIVENESS OF THE CT SHORTING LINKS REF: ANNEXUREII. | REF: ANNEXURE-II | 20. CALIBRATION OF PARAMETER – IF: INJECT 2 PHASE CURRENT TO THE FIELD CURRENT INPUT TERMINAL | OF BOTH CHANNELS OF DAVR AND MEASURE THE CORRESPONDING VOLTAGE LEVELS AT DAVR | REF ANNEXUREIII | 21. LIGHT LOAD TEST FOR CHECKING THE HEALTHINESS OF THE THYRISTORS DETAILS REF – | ANNEXURE IV. | PULSE INTERMEDIATE STAGE | 22. FIRING PULSES AT PULSE GENERATION UNIT | PULSE FINAL STAGE | WOULD BE CHECKED. | 23. CHECKING OF DC OUTPUT OF THE DAVR. | 24. OFFLINE CHECKING OF ALL LIMITER CIRCUIT IS TO BE DONE AS PER OEM PROCEDURES. | 25. RESTORATION OF PARAMETERS ALTERED DURING TESTING AND REVERIFICATION ALL TUNES | PARAMETERS. | 26. ALL PROTECTIONS AND INTERLOCKS WOULD BE CHECKED. | NOT MORE THAN 24 DEG C | HUMIDITY LESS THAN 55% RH | LESS THAN 55% RH | 27. AVR ROOM TEMPERATURE NOT MORE THAN 24 DEG C | SEALING AND CLEANLINESS SHALL BE ENSURED. ALARM FOR THE SAME IS TO BE PROVIDED | CONTROL | IN CONTROL ROOM FOR STATIONS WHERE EXCITATION CONTROL ROOM IS SEPARATE | 4.4 DYNAMIC TESTS | A PART1: | FOLLOWING TESTS WILL BE CARRIED OUT AT TURBINE SPEED 3000 RPM: | 1. MEASUREMENT OF THE PMG OUTPUT VOLTAGE AND PHASE SEQUENCE. | 2. MEASUREMENT OF PMG CURRENTS. | OCC | 3. CARRYING OUT OPEN CIRCUIT CHARACTERISTICS OCC AND SHORT CIRCUIT CHARACTERISTICS | SCC TESTS DETAILS REF – ANNEXURE – V. | SCC | DETAILS REF – ANNEXURE – V | 4. CHECK THE THYRISTOR CURRENT AND MV DROP ACROSS THYRISTORS. | B PARTII: | 1. AFTER CARRYING OUT OF SCC | OCC TESTS AND NORMALIZATION OF ALL SETTINGS | GOING FOR SYNCHRONIZATION CHANGE OVER FROM AUTO1 TO AUTO2 AND VICE VERSA | C PART – III: | 280-300MW | 1. PSS RESPONSE TEST NEEDS TO BE CARRIED OUT AT LOW LOAD280300MW | 2. PSS RESPONSE TEST NEEDS TO BE CARRIED OUT AT FULL LOAD 325375 MW | 325-375 MW | 3. PSS RESPONSE TEST NEEDS TO BE CARRIED OUT AT INTERMEDIATE LOAD400450MW | 400-450MW | D PART –IV: STEP TEST ON LOAD | - 3% | 3% IS TO BE DONE ON DIFFERENT LOADS | 1. STEP TEST + | 2. STEP TEST NEEDS TO BE CARRIED OUT AT LOW LOAD280300MW | 3. STEP TEST NEEDS TO BE CARRIED OUT AT FULL LOAD 325375 MW | 4. STEP TEST NEEDS TO BE CARRIED OUT AT INTERMEDIATE LOAD400450MW | E PARTV: LIMITER CHECKING ON LOAD | 1. LOW EXCITATION LIMITER | 2. ROTOR CURRENT LIMITER | 5.0 FREQUENCY OF CHECKING AND MEASUREMENTS | TESTS SHALL BE CARRIED OUT DURING UNIT OVERHAUL | AGM EM. | ANY DEVIATION SHALL BE REPORTED TO EM AND CAN BE DISPENSED WITH HIS APPROVAL. | 8.0 REVIEW | DOCUMENTS WILL BE REVIEWED ONCE IN TWO YEARS BY HOP. | 366215 | 09:40:52 | 202209:40:52 | SUBJECT:REVIEW OF LMI “ATTEMPERATOR SPRAY NOZZLES ANDB | LINERS O | DATE: 18.08.2022 | SUBJECT: REVIEW OF LMI “ATTEMPERATOR SPRAY NOZZLES AND LINERS” | THE ABOVE APPROVED LMI WAS PREPARED IN THE MONTH OF FEB.’2004. THE LMI WAS REVISED IN 2010 | 2020 AND 2021. THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER DETAILS AT REVISION INDEX OF | 2013 | LMI. | THE SUBNJECT LMI HAS BEEN REVIEWED. THE SUGGESTED CHANGES IN LMI AS PER COSISO00 | OGM | 02 REV01 AUG'22 HAVE BEEN CARRIED OUT. | MAY PLEASE ACCORD APPROVAL. | 12:22:16 | FOLLOWINNG CHANGES INCORPORATED IN REVISED LMI ATTACHED AS ANNEXURE NEW LMI | ATTACHED AS ANNEXURE -NEW LMI | A CLAUSE NO. 6.0: INSPECTION PROCEDURE INCORPORATED | B CLAUSE NO. 7.0: FIGURES OF SPRAY NOZZLES INCORPORATED | C ANNEXUREI: CHECKLIST FOR ATTEMPERATOR INSPECTION INCORPORATED | MAY PLEASE BE APPROVED | 17:08:11 | 17:27:03 | 14:53:45 | 16:12:37 | 16:18:15 | ISSUE NO.1; REVISION NO. 4.00; DATE: AUG’ 2022 | ATTEMPERATOR SPRAY NOZZLES | AND LINERS | IMPLÉMENTATION | 1.0 TITLE OF LMI ATTEMPERATOR SPRAY | NOZZLES AND LINERS | DATE ISSUE1; REV.4.00; AUG’2022 | 4.PREPARED BY | SENIOR MANAGER SIGNATURE | AGM BMD S IGNATURE_______________ | GM MTC. SIGNATURE_______________ | M SIGNATURE_______________ | 6. REVIEWED AND APPROVED BY SIGNATURE_______________ | TITLE: ATTEMPERATOR SPRAY NOZZLES AND LINERS | REV: 4.00 DATE: AUG’2022 | PAGE : 1 OF 7 | 8 EXCEPTION REPORTING 3 | AT SIMHADRI TWO SPRAY TYPE DESUPERHEATERS ARE INSTALLED IN THE CONNECTING LINK BETWEEN THE | SUPERHEATER LOW TEMPERATURE PENDANT OUTLET ER AND THE SUPERHEATER DIVISION PANEL INLET ER | FOR CONTROL OF MS TEMPERATURES. TWO SPRAY TYPE DESUPERHEATERS ARE INSTALLED IN THE REHEATER INLET | LEADS NEAR THE REHEATER INLET ER FOR CONTROL OF REHEATER TEMPERATURES. TEMPERATURE REDUCTION IS | ACCOMPLISHED BY SPRAYING WATER INTO THE PATH OF STEAM THROUGH A NOZZLE AT THE ENTERING END OF | DESUPERHEATER. | THERE HAVE BEEN REPORTED CASES OF CRACKING AND COMPLETE DETACHMENT OF ATTEMPERATOR | DUE TO FATIGUE STRAIN WHICH HAS RESULTED IN BLOCKAGE AND OVERHEATING OF | SPRAY NOZZLES | DOWNSTREAM TUBE ELEMENTS REQUIRING EXTENDED OUTAGES TO LOCATE AND REMOVE THE BROKEN | INCIDENTS OF ATTEMPERATOR LINER DETACHMENT AND DISPLACEMENT HAVE BEEN | PARTS. SIMILARLY | REPORTED RESULTING IN BLOCKAGE OF STEAM OUTLET FLOW AND TEMPERATURE IMBALANCE ACROSS THE | BOILER WIDTH. THE CRACKING OF NOZZLE WELDS AND LINERS IS NOT DETECTABLE DURING ROUTINE | PLANT MONITORING. | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH AN INSPECTION STRATEGY FOR ATTEMPERATOR SPRAY | MINIMIZE FORCED OUTAGES. | THE SCOPE OF THIS LMI IS TO DETAIL THE METS AND PERIODICITY THAT ARE TO BE ADOPTED FOR | THE INSPECTION OF ATTEMPERATOR SPRAY NOZZLES AND LINERS. | ATTEMPERATOR SPRAY NOZZLES AND LINERS REV: 2.00 DATE: APR’2013 | TO ACHIEVE THE OBJECTIVE OF THIS LMI | THE FOLLOWING APPROACH IS TO BE FOLLOWED: | A PERIODIC INSPECTION OF ATTEMPERATOR SPRAY NOZZLES AND LINERS WITH VIDEOSCOPE. | B REMEDIAL ACTIONS TO SUSTAIN INTEGRITY OF ATTACHMENTS ON DISCOVERY OF INTERNAL | CRACKS THROUGH VIDEOSCOPE INVOLVING CUTTING OF THE COAXIAL TUBE. | CTAKING AND SAVING SNAP SHOTS OF THE SPRAY NOZZLE AND LINER AND FILLING | PAGE : 3 OF 7 | A ALL THE SUPERHEATER AND REHEATER ATTEMPERATOR NOZZLES SHOULD BE INSPECTED | DURING OVERHAULS ONCE IN SIX YEARS USING DYE PENETRANT OR MPI FOR THE | INTEGRITY OF WELDS AS PER THE ATTACHED SH AND RH DESUPERHEATER | DRAWING. | FREQUENCY ONCE IN SIX YEARS | B ALL THE ATTEMPERATOR BODY LINERS SHOULD BE INSPECTED FOR STRUCTURAL RIGIDITY | AND FIXING ATTACHMENT INTEGRITY DURING OVERHAULS USING ENDOSCOPE | ONCE IN | SIX YEARS. | FREQUENCY ONCE IN FIVE YEARS | C STRENGTHENING OF WELDS | REPLACEMENT OF LINERS IS TO BE CARRIED OUT IF ANY | DEFECTS ARE OBSERVED DURING INSPECTION AS STATED ABOVE. | FREQUENCY AS AND WHEN NECESSARY | CRACKS IN NOZZLE WELDS | LINERS ENCOUNTERED DURING INSPECTION ARE TO BE | THE EXCEPTIONS CRACKS IN NOZZLE WELDS | LINERS | REPORTED AS PER THE FOLLOWING FORMAT TO O | DESCRIPTION OF UNIT LOCATION OF REMARKS | WITH PRESSURE PARTS. | 10. RECORD KEEPING | THE RECORDS TO BE MAINTAINED UNDER THIS LMI INCLUDE: | B REPORTS OF SURVEY AND RECTIFICATION WORK CARRIED OUT | C EXCEPTION REPORTING | THE ABOVE RECORDS ARE TO BE MAINTAINED BY PRESSURE PARTS | 11.REVIEW | THIS DOCUMENT SHALL BE REVIEWED BY HOP ON TWO YEARLY BASIS. | 12:21:22 | 370414 IDATE:19 | 202212:21:22 | SUBJECT:REVIEW OF LMI “BOILER ACCESS AND VIEWING ODOORS” | DATE: 19.08.2022 | SUBJECT: REVIEW OF LMI “BOILER ACCESS AND VIEWING DOORS” | ENG | THE ABOVE APPROVED LMI WAS PREPARED IN THE MONTH OF APRIL.’2020. THE LMI WAS REVISED IN THE MONTH OF | MAY ’2022. THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER DETAILS AT REVISION INDEX OF LMI. | 370414 | THIS LMNI HAS BEEN REVIEWED AND CHANGES WERE INCORPORATED IN THE DOCUMENT WITH REF NO | ISSUE1; REV.6.00; AUG’2022. | 001. | ORIGINAL REF DOCUMENT: OIN | APPROVAL MAY PLEASE BE ACCORDED. | 17:54:11 | HIGHLIGHTED | INCORPORATED IN REVISED LMI AS UNDER: | THE NECNESSARY CHANGES HIGHLIGHTED | PAGE NO. 4 CLAUSE 7.0 A | ANNEXURE 1 ADDED. | 09:55:54 | 10:28:06 | 15:41:33 | 16:03:37 | 12:20:26 | 14:23:13 | 15:06:23 | 058 | REVISION NO. 0; DATE: AUG’2022 | BOILER ACCESS | AND | VIEWING DOORS | 1.0 TITLE OF LMI BOILER ACCESS AND | DATE REV.0; AUG’2022 | REF.DOCUMENT COSISO00GN | 4.PREPARED BY: SENIOR MANAGER | AGM BMD SIGNATURE_______________ | 6. REVIEWED AND APPROVED BY | 8. INDEX LIST ENCLOSED. | 9. DISTRIBUTION LIST ENCLOSED. | TITLE: BOILER ACCESS AND VIEWING DOORS REV:0 | DATE: AUG’2022 | 058 PAGE : 1 OF 10 | 7.0 METOLOGY OF | 8.0 EXCEPTION REPORTING 4 | 10.0 RECORD KEEPING 4 | 11.0 REVIEW 4 | 12.0 REVISION INDEX 5 | 13.0 DISTRIBUTION LIST 6 | 14.0 COMPLIANCE RECORD 710 | 058 PAGE : 2 OF 10 | THE TWO PASS DRUM TYPE BOILER INSTALLED AT SIMHADRI IS PROVIDED WITH RANGE OF DOORS | LOCATED AT VARIOUS LOCATIONS TO PROVIDE ACCESS INTO THE BOILER OR ENABLE VIEWING OF BOILER | INTERNALS. THE ACCESS DOORS ARE PROVIDED FOR PROVIDING ACCESS TO PERSONNEL TO INSIDES OF | HELP IN EXAMINATION OF BOILER INTERNAL CONDITIONS WITH BOILER ONLOAD. THE BOILER HAS | SCAFFOLD DOORS AT 50M ELEVATION AND ACCESS DOORS AT 12.5 M OF FIRST PASS AND ACCESS DOORS | THE BOILER IS PROVIDED WITH VIEWING DOORS AT DIFFERENT ELEVATIONS OF FIRST PASS UP TO | DIVISIONAL PANEL BOTTOM. | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH A SYSTEM OF PERIODIC EXAMINATION AND | THE SCOPE OF THIS LMI IS TO DETAIL THE LOCATIONS AND METS THAT ARE TO BE ADOPTED FOR THE | PERIODIC INSPECTION AND RECTIFICATION OF BOILER ACCESS AND VIEWING DOORS. | SERVICESNTPC CORPORATE CENTER. | REV1 MARCH 2020 | BOILER ACCESS AND VIEWING DOORS OIN | THE OBJECTIVE OF THIS LMI IS SOUGHT TO BE ACHIEVED BY | A ENSURING READY ACCESSIBILITY TO ALL ACCESS AND VIEWING DOORS. | B PERIODIC INSPECTION AND RECTIFICATION TO ENSURE RELIABILITY. | 058 PAGE : 3 OF 10 | A ALL ACCESS DOORS AND VIEWING DOORS SHOULD BE READILY ACCESSIBLE WITHOUT DIFFICULTY | FACILITATING THE ABOVE. DOORS MODIFICATION FOR ACCESSIBILITY TO BE DONE AFTER | PROPER APPROVAL FROM COS AND ENGINEERING. | PR.PARTS | B ALL ACCESS AND VIEWING DOORS SHOULD BE CHECKED DURING OVERHAUL FOR | I FREENESS OF HINGES AND FASTENINGS | II INTEGRITY OF DOOR HANDLES | III REFRACTORY OF THE INSIDES OF DOORS | IV DOOR SEALS. | V ATTACHMENT WELDING TO BE DONE AS PER DRAWING. | THE ABOVE SHOULD BE SUITABLY RECTIFIED | IF FOUND DAMAGED. | PARTS | 326708 | 15:57:56 | 202215:57:56 | SUBJECT:LMI | 002POWER STATION DRAINAGE. REV.02 | APPROVBAL FOR | IMPLEMENTATIONREG. O | REV.2 HAS BEEN PREPARED BASED ON REVISED OGN REF. COSISO00OGN | AND IS ATTACHED HEREWITH. | THE SAME MAY PLEASE BE APPROVED BY COMPETENT AUTHORITY FOR IMPLEMENTATION. | 16:52:30 | MAY PLEASE BE MENTIONED | HIGHLIGHTED BEFORE GOING FOR FURTHER APPROVAL. ALSO SINCE | REVISEDN PORTIONS IF ANY | CLAUSE NO. 7 | PLEASE ROUTE | OF THE LMI | TABULATED ON PAGE NO 14 | THE RESPONSIBILTIY CENTRES ARE CLEARLY DEFINED | ALSO PLEASE MODIFY THE FILE ROUTING PATH | ALSO PLEASE MODIFY THE FILE ROUTING PATH THE LMI THROUGH THE CONCERNED | SECTIONS BEFORE FINAL | APPROVAL. | 18:15:56 | PL COMPNLY | 13:05:36 | CLAUSE NNO. 4.3.5 | 4.3.6 HAS BEEN MODIFIED AS PER THE REVISED OGN. | FILE ROUTED THROUGH CONCERNED | SECTIONS BEFORE FINAL APPROVAL BY COMPETENT AUTHORITY. | 18:41:18 | 09:26:24 | 16:33:54 | 17:22:56 | 17:42:45 | VISHWA MOHAN CHOUDHARY 003932 GENERAL MANAGER | 7588691232 | VMCHOUDHURY@NTPC.CO.IN | 15:46:55 | 18:21:21 | 17:27:08 | WATER IS NOT USED IN COOLING CIRCUIT | IN NTPNCSIMHADRI FOR GT AND OTHER POWER TRANSFORMERS COOLING | FOR GT | HENCE NO NEED OF SEPARATE ARRANGEMENT FOR ARCW WATER FOR GT AS STATED IN IN LMI . | 10:27:49 | 13:04:05 | ई के सी अरोड़ा अपर महाप्रबंधक | EEDA KALYAN CHAKRAVARTHY ARORA 006888 ADDL. GENERAL MANAGER | EKCARORA@NTPC.CO.IN | 9493124533 | 15:41:34 | 18:25:09 | 20:12:17 | 10:45:52 | REV. NO: 02; AUG’ 2022 | LMI FOR POWER SYSTEM | DRAINAGE | DATE REV. NO.: 02; AUG’2022 | DATE: MAY’2022 | NAME: SHRI. PVSN RAJU | NAME: SHRI. R.K. JHA | 7. APPROVED BY | 9. INDEX LIST ENCLOSED | 387427 | 17:39:48 | 202217:39:48 | SUBJECT:APPROVAL OF NEW LMI “THERMOGRAPHIC SURVEY OF BOBILER | FURNACE WALL | SCW TUBES” O | DATE: 25.08.2022 | SUBJECT: APPROVAL OF NEW LMI “THERMOGRAPHIC SURVEY OF BOILER FURNACE WALL | SCW TUBES” | LMI NO: COSISO00OGN | 055 GUIDELINES. | THIS IS A NEW LMI WHICH WAS PREPARED AS PER THE COSISO00OGN | THIS NENW LMI "THERMOGRAPHIC SURVEY OF BOILER FURNACE WALL | SCW TUBES" HAS BEEN PREPARED FOLLOWING | GUIDELINES RELATED TO THE DOCUMENT COSISO00OGN | 055. | THIS NEW LMI WITH REVISION NO0 MAY PLEASE BE REVIEWED AND APPROVED BY THE COMPETENT AUTHORITY. | 09:52:29 | THIS IS NA NEW LMI PREPARED BASED ON RECENTLY ISSUED OGN COSISO00OGN | LMI CHECKED AND SUBMITTED FOR APPROVAL | 09:19:41 | राजशेखर पाला अपर महाप्रबंधक | RAJASEKHAR PALA 005146 ADDL. GENERAL MANAGER | 8331015741 | PRAJSEKHAR@NTPC.CO.IN | 16:19:03 | 09:23:18 | ISSUE0; REV.0; AUG’2022 FOR "THERMOGRAPHIC | NEW LMNI NO. LMI | SURVEY OF BOILER FURNACE WALL | SCW TUBES " FOR NTPC SIMHADRI 500 MW BOILERS | PLEASE BE ACCORDED APPROVAL. | 12:31:27 | 13:15:42 | 15:22:26 | ISSUE NO.0; REVISION NO. 0; DATE: AUG’2022 | THERMOGRAPHIC SURVEY OF | BOILER FURNACE WALL | SCW | 1.0 TITLE OF LMI THERMOGRAPHIC SURVER OF | SCW TUBES | ISSUE0; REV.0; AUG’2022 | TITLE: THERMOGRAPHIC SURVER OF BOILER FURNACE WALL | REV:0 DATE: AUG’2022 | REF NO. COSISO00OGN | 055 PAGE : 1 OF 10 | 14.0 DRAWINGS 710 | TITLE: | THERMOGRAPHIC SURVER OF BOILER FURNACE WALL | 055 PAGE : 2 OF 10 | A THERMOGRAPHY SURVEY IS PERFORMED TO INSPECT THE EXTERNAL SURFACE OF THE BOILER TUBE WALL | FLOW RESTRICTIONS. IT IS ONE OF THE POTENT TOOL TO | TO IDENTIFY AND QUANTIFY POSSIBLE HOT SPOTS | DETECT PARTIAL TO FULL RESTRICTIONS IN WATER | STEAM FLOW PATH OF BOILER TUBES BY MONITORING TUBE | EXPERIENCING HIGH TEMPERATURE | IDENTIFYING IT FOR CLEANING DURING NEXT OPPORTUNITY | SHUTDOWN AND THEREBY AVOIDING BOILER TUBE FAILURES DUE TO OVERHEATING. THE THERMOGRAPHY | SCAN PROVIDES A ‘PICTURE’ OF SURFACE TEMPERATURE DISTRIBUTION ACROSS THE SCANNED AREA WITH | BENDS AND SPIRAL TO VERTICAL | PARTICULAR ATTENTION BEING PAID TO THE AREAS AROUND BUTT WELDS | WALL FORGE FITTINGS WHERE POTENTIAL DEBRIS MAY COLLECT AND CAUSE BLOCKAGE. | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH A SYSTEM FOR THERMOGRAPHIC SURVEY OF BOILER | SCW TUBES OF THE BOILER. | COMPLETE | THE SCOPE OF THIS LMI IS THERMOGRAPHY SURVEY PARTIAL | PARTIAL | COMPLETE OF THE BOILER FURNACE WALL | SCW TUBES OF BOILER TO KNOW FLOW RESTRICTION IN BOILER TUBES. | NOT APPLICABLE | A ENSURING AVAILABILITY OF THERMOGRAPHIC IMAGING CAMERA WITH INFRARED DETECTION | CAPABILITY ALONG WITH ITS CALIBRATION CERTIFICATES. | B EXAMINATION AND SURVEY OF THE AREA TO BE DONE ALONG WITH SAFE ROUTE FOR ESCAPE | IN CASE OF ANY MISHAPPENING WITH ARRANGEMENT FOR FIRE PREVENTION AND SAFETY | PERSONNEL. | 055 PAGE : 3 OF 10 | A THE BOILER MUST BE IN STARTUP CONDITION FOR ANY SIGNIFICANT OBSTRUCTION. | MEASURE INDIVIDUAL TUBES TEMPERATURE AS PER ATTACHED DRAWING. | SCW TUBES AS DETAILED IN THE LMI IS WITH PRESSURE PARTS | 28342 | D08 | 18:01:04 | 202518:01:04 | TREATMENT PLANT NTPC SIMHADRI LMI NO: LMIOGNENOV011 | SIMHADRI LMI NO: LMI | ENV | NEXT REVIEW WILL BE IN THE MONTH OF MARCH 2027 OR IF THE OGN IS REVISED WHICHEVER IS EARLIER. | PUT UP FOR THE APPROVAL OF COMPETENT AUTHORITY AND FOR THE IMPLEMENTATION. | FORWARDED FOR APPROVAL PLEASE. | SUBMITNTED FOR REVIEW BY CONCERN S FOR ANY REMARK AND FOR APPROVAL BY CA PLEASE. | 10:05:58 | 10:22:45 | CHANGES HAS BEEN DONE AS PER THE STANDARD FORMAT. | AS MENNTIONED IN THE PREVIOUS PAGE | ATTACHED DOCUMENT UPDATED. | MAY PLEASE SEE AND FORWARD FURTHER. | 12:07:16 | 17:23:14 | 09:44:33 | 16:36:19 | LMI HANS BEEN MODIFIED AS PER THE LATEST FORMAT. | 12:20:55 | 09:59:46 | 16:14:01 | 19:14:39 | MAY PLENASE REVIEW. | पी गंगाधर अपर महाप्रबंधक | PADALAHARIVEERA GANGADHAR 008164 ADDL. GENERAL MANAGER | PHVGANGADHAR@NTPC.CO.IN | 9650998462 | 18:21:16 | FORWARDED FOR FURTHER PROCESS. | 16:12:27 | PL REVIENW | नीरज कुमार अपर महाप्रबंधक | NIRAJ KUMAR 007109 ADDL. GENERAL MANAGER | 9650997827 | NIRAJKUMAR01@NTPC.CO.IN | 16:42:44 | THE LMNI HAS BEEN REVIEWED AND FOUND TO BE IN LINE WITH THE OGN. | हरीकृष्ण सुररपु उप महाप्रबंधक | HARIKRISHNA SURARAPU 095655 DY. GENERAL MANAGER | SHKRISHNA@NTPC.CO.IN | 9437020867 | 12:09:19 | 11:23:57 | FORWARDED PLEASE. | 17:03:33 | NO CHANNGES HAVE BEEN PROPOSED IN REVIEWED LMI. ONLY LMI FORMAT CHANGED AS PER OGN. | 17:34:38 | 18:00:12 | 16:11:27 | प्रसन्ता कुमार जेना मुख्य महाप्रबंधक | PRASANTA KUMAR JENA 006081 CGM | 17:12:27 | 779479 | D21 | 10:28:42 | 202310:28:42 | SUBJECT:APPROVAL FOR REVISION OF LMI ON GUIDELINES FOR COAL MILL AND BBUNKER | HAS BEEN REVISED VIDE “LMI | ISSUE NO.1; | 052 | ATTACHED AT NTPC SIMHADRI | REVISION NO. 1.00 | DATE: JAN'2023”.AS PER LMI | 2YEARLY REVIEW WAS DUE IN DECEMBER'22. | • THE FOLLOWING MODIFICATIONS HAVE BEEN MADE IN THE DOC: | POINT NUMBER4 | CHECKLIST –III | 2. CLAUSE 6.4 PERFORMANCE CHECKS | FREQUENCY HAS | BEEN MODIFIED TO 3 MONTHS FROM EARLIER SIX MONTHS. | POINT NUMBER5 HAS BEEN ADDED | 3. CLAUSE 6.4 PERFORMANCE CHECKS | POINT NUMBER10 HAS BEEN ADDED | 4. CLAUSE 6.4 PERFORMANCE CHECKS | 5. CLAUSE 6.5 MILL HEALTH MATRIX CHECKLIST –IV HAS BEEN ADDED. | 6. CLAUSES 6.6 BEST PRACTICES IN MILLING SYSTEM POINT NO O TO Y HAS BEEN ADDED. | 7. A NEW CLAUSE NO7.0 "INSPECTION | ADDED. | 8. THE LMI HAS BEEN REVISED AS PER NEW DOCUMENT "OGN | 052 REV. NO.: 1 NOV. | 2022". | • SUBMITTED FOR APPROVAL OF BUH PLEASE. | 09:32:41 | THE LMNI HAS BEEN REVISED. NECESSARY CHANGES DONE IN LMI ARE MENTIONED AT PAGE1 OF NOTE. | 10:41:58 | MAY PL.N SEE. | 16:40:00 | 17:58:09 | 18:13:24 | AS PEATNTACHED REVISED LMI | AT PAGE NO. 10 UNIT OF MEASUREMENT MAY PLEASE BE MENTIONED. | 18:29:26 | 23:48:11 | IN ATTACNHED REVISED LMI AT PAGE NO 10 | 10:30:05 | NECESSANRY CHANGES REGARDING UNIT OF MEASUREMENT DONE AT PAGE NO. 10 IN LMI DOCATTACHED. | 16:43:01 | FPR REVNIEW AND FURTHER APPROVAL PLEASE. | 09:47:40 | 12:21:14 | REVIEWNED AND FOUND OKAY. | के कृष्णा रेिड़़्ड़़ अपर महाप्रबंधक | K KRISHNA REDDY 032588 ADDL. GENERAL MANAGER | KKRISHNAREDDY@NTPC.CO.IN | 9440901769 | 17:28:48 | 11:35:57 | 10:45:50 | 20:34:47 | FILE CLOSED BY: | 12:05:27 | 202312:05:27 | REV: 1.00 DATE: JAN ’23 | ISSUE NO.1; REVISION NO. 1.00; DATE: JAN’2023 | GUIDELINES FOR COAL MILL AND | GUIDELINES FOR COAL MILL AND BUNKER | DATE ISSUE1; REV: 1.00; JAN’2023 | REV. NO.: 1 NOV. 2022 | BMD MILLS SIGNATURE | BMD- MILLS | BMD-MILLS | 5. CHECKED BY: DGM BMDMILLS SIGNATURE | AGM CHEM SIGNATURE | GM O SIGNATURE | 202316:20:52 | 746909 IDATE:09 | 16:20:52 | COAL LMI | SUBJECT:LMI ON SAMPLING AND ANALYSIS OF COAL REVISED O | "LMI ON SAMPLING AND ANALYSIS OF COAL" | LMI DOC NO. LMI CHEM | REVISION 4 | HAS BEEN REVISED IN LINE WITH COSISO00OGN | 006 REV. NO.: 5 NOV. 2022. | THE FOLLOWING CHANGES ARE BEING DONE IN THE REVISED LMI : | REGARDING THE STANDARD TEST METS. | B. EMPANELMENT OF THIRDPARTY SAMPLING AGENCIES AT MINE END AND UNLOADING END AS PER LATEST CIRCULAR BY | MOP INCLUDED. | C. IMPORTED COAL SAMPLING MODALITIES HAVE BEEN CHANGED AS PER THE LATEST GUIDELINES. | D. COAL AS FIRED SAMPLING SECTION AND DISPOSAL FREQUENCY HAS BEEN INCLUDED. | E. GENERAL GUIDELINES INCLUDED IN ANNEXURE1 FOR ISOLATION OF OHE FOR WAGON TOP SAMPLING. | THE DOCUMENT ENCLOSED FOR KIND PERUSAL AND APPROVAL PLEASE. | 746909 | 17:03:05 | 19:32:56 | AMULYA KUMAR BEHERA 097433 ADDL. GENERAL MANAGER | 9425534368 | AMULYABEHERA@NTPC.CO.IN | 10:53:16 | 09:51:10 | 11:56:18 | 15:28:12 | LMI CHEM | NTPCSIMHADRI | LMI ON SAMPLING AND ANALYSIS OF COAL | APPROVED FOR IMPLEMENTATION BY GGM SIMHADRI | SAMPLING AND ANALYSIS OF COAL | S.NO. DESCRIPTION PAGE | NOS. | 1 INTRODUCTION 3 | 2 SUPERSEDED DOCUMENTS 3 | 3.1 SCOPE 3 | 4.1 COAL AS FIRED SAMPLING | PREPARATION 5 | PREPARATION AT MINES 6 | 4.2 DOMESTIC COAL SAMPLING | 4.3 COLLECTION OF SAMPLES FROM WAGONS 8 | 4.4 COLLECTION OF SAMPLES OF COAL DISPATCHES BY 10 | ROAD | 4.5 STACK YARD COAL SAMPLING 11 | 4.6 PREPARATION OF DOMESTIC COAL SAMPLES 11 | 4.7 PREPARATION OF TOTAL MOISTURE SAMPLE AND 12 | DETERMINATION OF TOTAL MOISTURE | 4.8 MODALITIES FOR IMPORTED COAL QUALITY 12 | DETERMINATION | 4.9 IMPORTED COAL SAMPLING GUIDELINES FOR NTPC 13 | SIMHADRI STATION END SAMPLE COLLECTION: | 5.0 CORRECTIONS ON QUALITY VARIATIONS 15 | 5.1 GROSS CALORIFIC VALUEBASED GRADING SYSTEM 16 | SAMPLES ANALYSIS | 5.3 REPORTING OF RESULTS 17 | 5.4 CRITERIA FOR REJECTION OF SUSPECT TEST RESULTS 18 | REFERENCES 19 | 5.5 ASSOCIATED DOCUMENTS | ALSO FOR | IN COAL FIRED POWER STATIONS | SYSTEM IS ONE THAT COLLECTS A REPRESENTATIVE SAMPLE AND FROM WHOLE QUANTITY OF THE COAL IN | CONSIDERATION. FOR WHICH MINIMUM SPECIFIED NUMBER OF INCREMENTS OF SPECIFIED WEIGHT | SPECIFIED INTERVAL SHALL BE COLLECTED. | PREPARATION AND | CORRECT QUALITY EVALUATION OF COAL DEPENDS ON ITS REPRESENTATIVE SAMPLING | ANALYSIS. ACCURATE ANALYSIS AND REPORTING OF RESULTS IS ESSENTIAL TO EVALUATE THE ORIGINAL COAL | QUALITY AND THE PURPOSE FOR WHICH IT IS INTENDED. | 2.0SUPERSEDED DOCUMENT | DOMESTIC | 3.1 SCOPE: THIS LMI PROVIDES GUIDELINES FOR SAMPLING AND TESTING OF COAL AS FIRED | IMPORTED COAL | PROVIDES STANDARDS THAT ARE BEING IN USE FOR | COAL FROM STACK PILES. ALSO | COAL | TESTING PROCESSES. | PREPARATION | SAMPLING | PAGE 4 | 1. ENSURING COLLECTION AND PREPARATION OF COAL AS FIRED SAMPLES | 2. ENSURING THAT SAMPLES OF DOMESTIC COAL ARE COLLECTED BY THE | SAMPLING AT LOADING END AND UNLOADING ENDS AS PER SECTION | 4.2 | 3. ENSURING COLLECTION OF DOMESTIC COAL SAMPLES FROM WAGONS – FM | 4. COLLECTION OF COAL SAMPLES DISPATCH BY ROAD MODE 4.4 – FM | 5. ENSURING COLLECTION OF SAMPLES FROM STOCK YARD PILES AS PER – FM | 6. PREPARATION OF DOMESTIC COAL SAMPLES AS PER 4.6 | 7. PREPARATION OF TOTAL MOISTURE SAMPLE AND DETERMINATION OF | 8. MODALITIES FOR IMPORTED COAL QUALITY DETERMINATION AS PER 4.8 | 9. IMPORTED COAL SAMPLING GUIDELINES FOR NTPC SIMHADRI – FM | 10. CORRECTIONS BASED ON QUALITY VARIATIONS AS PER 5.0 – FM | PAGE 5 | PREPARATION: | 4.0 COAL SAMPLING | COAL AS FIRED SAMPLING RESULTS REQUIRED FOR THE INTERNAL MONITORING OF THE IMPACTS OF COAL QUALITY | RELATED TO COMBUSTION CHARACTERISTICS AND EFFICIENCY ISSUES AND TO ASCERTAIN THE BLENDING RATIO FOR | THE STATIONS WHERE BLENDED COAL IS FIRED. COAL RECEIVED IN POWER STATION IS CRUSHED AND FED TO | COAL SAMPLE COLLECTED BEFORE BUNKERING | FIRING IS TERMED AS COAL AS FIRED SAMPLE. IN | BUNKERS | ORDER TO TAKE REPRESENTATIVE COAL SAMPLE OF COAL AS FIRED THE SAMPLING POINT SHOULD BE SAFE | EASILY ACCESSIBLE AND CONVENIENT FOR COLLECTING THE SAMPLE. | V YEAR | FOR EACH PAT ASSESSMENT | V YEAR COAL AS FIRED SAMPLING AND TESTING IS TO BE CARRIED OUT AS | PER ISSUED GUIDELINES FOR PATII CYCLE. | 4.1.1 COLLECTION OF SAMPLES FROM FEEDERS: | A COAL AS FIRED SAMPLE CAN BE COLLECTED MANUALLY FROM SAMPLING PORTS AT THE INDIVIDUAL GRAVIMETRIC | VOLUMETRIC FEEDER | FROM THE BUNKER TO INDIVIDUAL MILLS AT EQUAL INTERVAL IN ALL THREE SHIFTS. | B ENOUGH COAL QUANTITY NOT LESS THAN 450 KGS | DAY IS COLLECTED FROM THE FEEDERS. | C THE SAMPLE SHALL BE COLLECTED IN 5 NUMBER OF INCREMENTS WITH 4 KG SAMPLE PER INCREMENT. | 4.1.2 PREPARATION OF SAMPLE: | PICTURE 1 | PAGE 6 | QUARTERING REDUCTION TILL 2 KG. | C FINALLY | THE PROCESS DEPICTED IN PICTURE -1 | SIZE BY PULVERIZER. THE PROCESS DEPICTED IN PICTURE 1. | D EXCESSIVE GRINDING OF SAMPLE SHALL BE AVOIDED AS ITIS HARMFUL. | E WHEN IMPORTED COAL IS FIRED | COAL AS FIRED SAMPLE FOR INDIVIDUAL FEEDER IS CARRIED OUT ON | WEEKLY BASIS. | VM % OF FEEDER COAL NEEDS TO BE MONITORED. | G THE TESTING FREQUENCY IS ON DAILY BASIS AND REPORTING SHALL BE ON STAGEWISE AS PER THE TABLE | GIVEN IN PICTURE – 2 REFERENCE: COSISO00OGN | 015 CODE OF PRACTICE ON POWER | TABLE 1 | 4.2 THIRD PARTY COAL SAMPLING MODALITIES AND SAMPLE PREPARATION: | THE THIRDPARTY COAL SAMPLING PROCEDURE HAS BEEN JOINTLY AGREED BETWEEN NTPC AND COAL | SUPPLIER AND CIMFR AND FORM PART OF FUEL SUPPLY AGREEMENT. THE PROCEDURES AS DESCRIBED | ARE BASED ON FSA | BIS STANDARDS. | NTPC AND | TRIPARTITE | CIL | IN CASE THIRD PARTY COAL SAMPLING AGREEMENT TRIPARTITE AMONG SUPPLIER CIL | CIMFR IS IN PLACE THEN AT LOADING END SAMPLING WILL BE DONE BY CIMFR AS PER THE SIGNED | AGREEMENT. COLLECTION OF SAMPLES AT UNLOADING POINT WILL BE DONE BY CIMFR AS PER BILATERAL | AGREEMENT. | 4.2.1 COAL SAMPLING PROCEDURE CIMFR BASED THIRD PARTY SAMPLING: | CIMFR BASED THIRD PARTY SAMPLING | A THE DETAILED MODALITIES FOR THIRD PARTY SAMPLING PROCEDURES WHICH HAVE BEEN JOINTLY | AGREED BETWEEN NTPC AND COAL SUPPLIER AND FORM PART OF FUEL SUPPLY AGREEMENT | SECI | RELEVANT IS 436PARTI | SCHEDULE V | 1964 SPECIFICATION OR ITS LATEST VERSION ARE | TO BE FOLLOWED FOR COAL SAMPLE PREPARATION AND ANALYSIS | FOR DETERMINATION OF COAL | QUALITY FOR PAYMENT PURPOSE. NOTE: THE PROCEDURE MAY CHANGE AT TIME OF REVIEW IN | FUEL SUPPLY AGREEMENT. | B SAMPLES OF COAL SHALL BE COLLECTED BY THE THIRD PARTY EITHER MANUALLY OR THROUGH ANY | LOADING POINT | AT EACH OF THE DELIVERY POINTS LOADING POINT FOR | DETERMINING THE QUALITY OF COAL IN PRESENCE OF REPRESENTATIVES OF NTPC AND COAL | INDIA. | C T A B LE 1 1 | T E S T IN G FR E Q | D A S .N . | S A | O T E : | C O A L A S F | S A M P LIN G | U E N C Y : D | T E O F | M P L IN G | IR E D S A M | A N A LY | A ILY B A | Q T Y | M T | P LIN G A | S IS O F C | S IS | N D | O A | S T A G E W IS | T O T A L | M O IS T U | T E S T IN G M | L” . | A LIT IE S | A S H | S H A LL B E A S | V M | P E | R O G | F C | T M B A S | N O P S C | E M | G C V | K C A | 0 0 | 6 O | “ G U ID E | R E | LIN | E S | R K | 674289 | 17:17:39 | 202217:17:39 | PITCH AXIAL FANS O | 051 | 051" REV. NO.: 1 OCT. 2022. | ALL APPNLICABLE REVISIONS INCORPORATED AS PER REVISED OGN. | 17:48:27 | THE NEWN LMI HAS BEEN REVISED AS PER REVISED OGN. | THE REVISIONS MADE IN LMI HAVE BEEN MENTIONED IN ATTACHED DOCUMENT LMI ON O | M OF VARIABLE PITCH | AXIAL FANS REV1 DEC'22 AT PAGE NO. 19 REVISION INDEX. | 08:45:15 | 15:59:33 | THE LAST SUBCLAUSE UNDER 4.1 IS 4.1.12 | IN THE RNEVISED LMI | WHILE IN ITS REVISION INDEX IT SHOULD BE READ IN AS | PAGE NO. 21 AND NOT PAGE19 THE SAME IS MENTIONED AS 4.1.13. PLEASE CONFIRM THE CORRECT SUB CLAUSE NO. AND | MAKE NECESSARY CORRECTION IN THE REVISED LMI. ALSO PAGE NO '19' IS REPEATING THREE TIMES AT THE FAG END | SHEETS OF THE REVISED LMI. IT SHOULD READ PAGE NO.19 | 21. PLEASE CORRECT THE SAME IN THE REVISION | AFTER NECESSARY CORRECTIONS. | ENCLOSED IN THE ANNEXURES. REST IS OK. KINDLY RESUBMIT THE REVISED LMI | 19:39:08 | PLEASE DNO THE NECESSARY CORRECTIONS AS PER PREPAGE | 08:51:28 | LMI REVNISED AND ATTACHED AFTER NECCESSARY CORRECTIONS. | 11:20:00 | THE NECNESSARY CORRECTIONS DONE I.E. CLAUSE NO CHANGED TO 4.12 INSTEAD OF 4.13 IN REVISION INDEX AND PAGE | NUMBERING 1921 CORRECTED. | 15:55:56 | 16:11:18 | 11:37:47 | 11:56:54 | REVISION 01 | DEC’ 2022 | GUIDELINES FOR VARIABLE PITCH | AXIAL FANS | REV.NO.:1 DATE: DEC’ 2022 | DEC’ 2022. | 1 TITLE OF LMI | FOR VARIABLE PITCH AXIAL FANS. | REV. NO.: 1 OCT’ 2022 | 6 RECHECKED BY | 11 DISTRIBUTION LIST ENCLOSED | CHEM LMI | 300846 | 202510:38:17 | 10:38:17 | D10 | UP PRACTICES O | SHUT DOWN AND LAYUP | PRACTICES HAS BEEN REVISED BY CCOS. | PREVIOUS LMI VERSION PRESENT LMI VESRION | 065 ; REV. NO.: 0 | 017 REV. NO.: 2 FEB. 2023 COSISO00OGN | 1. MONITORING OF CONDENSATE ACC | DCC FOR BOILER FILLING AND LIGHTUP CLEARANCE HAS BEEN INCORPORATED IN | DRUMTYPE UNITS. | 2. A NEW CLAUSE HAS BEEN ADDED FOR HOT WELLDEAERATOR CLOSED CIRCULATION. | 3. MONITORING OF THE MAIN STEAM CC FOR TURBINE ROLLING CLEARANCE HAS BEEN ADDED. | 5. GUIDELINES FOR INSTALLING AN AUTOMATIC PRESSUREREDUCING SYSTEM FOR SWAS SAMPLES IN UNITS WITH LOW | SAMPLE FLOW DURING CYCLIC LOADING HAVE BEEN ADDED. | 6. ADDITIONAL PI TAGS FOR SUBCRITICAL AND SUPERCRITICAL UNITS. | 250 | 7. CONDENSATE DUMPING PIPELINE DIMENSIONS FOR 110 | 500 | 600 | 800MW UNITS HAVE BEEN ADDED IN | 210 | ANNEXURE. | DRAFT LMI | OGN ARE ATTACHED FOR REFETRENCE. | PUT UP FOR KIND APPROVAL OF CA FOR IMPLEMENTATION. | DRAFT LNMI IS INITIATED. COPY OF DRAFT LMI AND OGN IS ATTACHED. | 10:49:48 | 19:52:16 | 11:00:06 | NECESSANRY MODIFICATION DONE AS PER THE GUIDELINEDS MENTIONED IN LMI | 002. | PUT UP FOR THE APPROVAL PLEASE. | 17:06:52 | ERN ON EVERY PAGE SHOULD MENTION REV. NO. ALONG WITH LMI NO. | 10:58:12 | NECESSANRY CHANGES INCORPORATED. | 18:16:46 | LMI IS NIN LINE WITH THE REVISED OGN. | 11:25:20 | 13:56:48 | LMI REVNISED VERSION IS IN LINE WITH THE OGN DOCUMENT. MAY PLEASE BE PROCESSED FURTHER. | 18:55:05 | MAY KINNDLY REVIEW | नीलांजन मंड़ल अपर महाप्रबंधक | 11:46:45 | 17:05:55 | 10:01:35 | 11:27:10 | I POINTS IN LINE WIH ATTCHED OGN. | REVIEWNED C | राजेश मंडावी विरष्ठ प्रबंधक | RAJESH MANDAVI 075056 SENIOR MANAGER | 9425222133 | RAJESHMANDAVI@NTPC.CO.IN | 19:23:57 | 20:02:51 | 16:30:06 | LMI IS NIN LINE WITH THE OGN. | SUBMITTED FOR KIND APPROVAL | PLEASE. | 21:43:38 | 374239 | 202318:23:54 | SUBJECT:LMI REVISION HIGH CURRENT BUS BAR SYSTEM CONNECTED TO GENERATOBR AND | GENERATOR TRANSFORMER LMI | 035 O | 035 | LMI OF HIGH CURRENT BUS BAR SYSTEM CONNECTED TO GENERATOR AND GENERATOR TRANSFORMER | 035 REV. NO.: | 035 IS REVISED BASED ON LATEST OGN COSISO00OGN | 1 AUG. 2022 | BOTH REVISED LMI AND OGN ARE ATTACHED HEREWITH. | िमलनकुमार माझी विरष्ठ प्रबंधक | MILAN KUMAR MAJI 101811 SENIOR MANAGER | 9434067642 | MKMAJI@NTPC.CO.IN | PUT UP FNOR APPROVAL PLZ. | 18:25:02 | REVIEWNED AND FOUND IN LINE WITH OGN | 35. | 17:25:08 | TRANSFORMER | GENERATOR AND SWITCHYARD GROUP FOR REVIEW. | ROUTEDN THROUGH HT | 18:58:26 | REVIEWNED AND FOUND IN LINE WITH OGN. | 16:26:24 | CHECKEDN AND FOUND IN LINE WITH OGN | 10:14:52 | CONNECTED TO GENERATORS AND GENERATOR TRANSFORMERS. | MAY APPROVE. | 10:23:48 | REVIEWNED AND FOUND IN ORDER | 19:12:47 | 17:32:33 | 09:33:37 | 18:12:11 | BE NOTED AND FORWARD FOR FURTHER APPROVAL | 11:42:58 | CLUASE NO. 7.1 | 7.2 ARE SAME AND REPEATING IN LMI. | वेलु सेंिथल कुमार उप महाप्रबंधक | VELU SENTHILKUMAR 085505 DY. GENERAL MANAGER | 9446004620 | VSENTHILKUMAR@NTPC.CO.IN | 18:49:25 | REVIEWNED AND FORWARDED FOR FURTHER APPROVAL. | 09:58:13 | 18:00:02 | 17:23:04 | REVIEWNED AND FORWARDED FOR FUTHER APPROVAL | 18:10:09 | 23:27:00 | 09:07:01 | 09:41:03 | 602862 | 202208:53:48 | 08:53:48 | SUBJECT:APPROVAL OF LMI BOILER ER LIGAMENT CRACBKING | GUIDANCE ON INSPECTION POLICY O | DATE: 17.11.2022 | SUBJECT: REVIEW OF LMI “BOILER ER LIGAMENT CRACKINGGUIDANCE ON | INSPECTION POLICY” | THE ABOVE APPROVED LMI WAS REVISED IN THE MONTH OF JULY.’2022. THE ENVISAGED CHANGES IN LMI ARE | MAY PLENASE PROVIDE APPROVAL FOR THE REVISED VERSION OF SUBJECT LMI DOCUMENT WITH REV5. | 20:06:46 | CHANGENS INCORPORATED AS PER REVISED LMI: | 1. ECO ER FIGURE ADDED | 2. ECO ER INCLUDED IN LOW RISK ER | 3. INSPECTION OF UNCRACKED ER ELABORATED | 4.ANNEXUREA CHECKLIST ADDED FOR BOILER ER LIGAMENT CRACKING | THE REVISED LMI DOC NEW LMI ATTACHED MAY PLEASE BE APPROVED. | DOC- NEW LMI ATTACHED | 09:14:42 | 09:32:14 | REVISEDN LMI | MAY PLEASE BE ACCORDED APPROVAL. | 10:53:06 | 11:45:44 | 12:34:34 | ISSUE NO.1; REVISION NO. 5.00; DATE: NOV’2022 | BOILER ER LIGAMENT | CRACKING GUIDANCE ON | INSPECTION POLICY | 1.0 TITLE OF LMI BOILER ER LIGAMENT | NOVEMBER 2022 | DATE REV. NO.: 5 | SIGNATURE_______________ | DGMBMD | GM MTC. | SIGNATURE____ | 9.DISTRIBUTION LIST ENCLOSED. | TITLE: BOILER ER LIGAMENT CRACKING – GUIDANCE | ON INSPECTION POLICY REV 5.00 DATE:NOV’2022 | 14.0 COMPLIANCE RECORD 7 | ON INSPECTION POLICY REV 5.00 DATE: NOV’2022 | THE NEED TO OPERATE FOSSIL POWER PLANTS IN A FLEXIBLE MANNER HAS RESULTED IN THE | APPEARANCE OF THERMAL FATIGUE DAMAGE IN THE COMPONENTS SUCH AS STEAM ERS. | BECAUSE THE COST OF REPLACING SUCH COMPONENTS CAN BE HIGH AND LEAD TIMES FOR THEIR | THERE IS AN INCREASED NEED FOR AN INSPECTION STRATEGY THAT CAN LOCATE | MANUFACTURE LONG | AND MONITOR FLAW GROWTH SO THAT INFORMED DECISIONS CAN BE MADE ON THE INCIDENCE OF | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH AN INSPECTION STRATEGY FOR LIGAMENT CRACK | THE ER LIGAMENT CRACK INSPECTION OF STEAM ERS. STEAM ERS ARE DIVIDED INTO | THE COLLECTING ER | TWO CATEGORIES A HIGH RISK I ALL SUPER HEATER STAGE ERS I.E. | AT THE OUTLET OF A SUPERHEATER STAGE OF TUBING OPERATING ABOVE DRUM SATURATION | TEMPERATURE AND II ALL ERS IN HORIZONTAL SELFDRAINING SUPER HEATERS WHICH OPERATE | ALL SUPER HEATER | ABOVE 400 DEGREE C B LOW RISK I.E. | ECONOMISER AND REHEATER STEAM | ERS NOT IDENTIFIED IN THE HIGHRISK CATEGORY. | BOILER ER LIGAMENT CRACKING – GUIDANCE ON | INSPECTION POLICY REV 2.00 DATE:APR'2013 | TO ACHIEVE THE OBJECTIVE OF THIS LMI THE FOLLOWING APPROACH IS TO BE FOLLOWED: | A PERIODIC INSPECTION OF ER LIGAMENTS FOR CRACKS. | C REINSPECTION OF LOWRISK ERS ONLY IF CRACKING DETECTED IN PREVIOUS | INSPECTION. DPT | MPI OF ALL STUBS OF ECONOMIZER INLET ER IN OVERHAULING. | IINSPECTION PROCEDURE TO BE ADOPTED | A DURING OVERHAULS | I VISUAL INSPECTION OF SURFACE FOR ANY CRACKS | II LPT AT SUSPECTED LOCATIONS TO DETERMINE THE SIZE OF THE SURFACE CRACK AND | RECORDING THE SAME TO FACILITATE CRACK GROWTH MONITORING. | B DURING RLA STUDIES | I AN INITIAL INTERNAL VISUAL INSPECTION OF ER TO BE CARRIED OUT USING | BOROSCOPE. | AN ULTRASONIC THICKNESS INSPECTION SHALL BE CARRIED OUT | II IF CRACKING IS PRESENT | TO DETERMINE THE CRACK SIZES AND PROFILES | PR .PARTS GROUP | II INSPECTION STRATEGY TO BE ADOPTED | A FOR UNCRACKED HIGHRISK ERS : | IA DURING EVERY OVERHAUL | IC REINSPECTED AT OR BEFORE TWICE THE NUMBER OF STARTS AS AT FIRST | ANTLERS TUBES EVERY OVERHAULING. | INSPECTION. IOT | DPT TO BE DONE FOR TERMINAL | B FOR CRACKED HIGH RISK ERS WHERE CRACK GROWTH IS TO BE MONITORED : | IB EVERY TWO YEARS | GEOMETRY IMPROVEMENTS : | IB AT HALF THE NUMBER OF STARTS OF THE LIFE OF ORIGINAL ER | D FOR HIGHRISK ERS REPLACED WITH 9% CR STEEL ER: | IB AT TWICE THE NUMBER OF STARTS OF THE LIFE OF ORIGINAL ER | E FOR LOWRISK ERS: | PR. PARTS GROUP | IIIACTIONS IN CASE AN INTERNAL CRACK IS DISCOVERED | A PROVIDE A SAFETY CASE AROUND THE ER | IF DEEMED NECESSARY | INTERNAL LIGAMENT CRACKS | THE EXCEPTIONS INTERNAL LIGAMENT CRACKS ENCOUNTERED DURING INSPECTION ARE TO BE | REPORTED AS PER THE FOLLOWING FORMAT AND TO BE TAKEN UP WITH CORPORATE ENGG | MANUFACTURER BMD | DESCRIPTION OF UNIT ER LOCATION OF REMARKS | EXCEPTION NO. DESCRIPTION EXCEPTION | THE ABOVE RECORDS ARE TO BE MAINTAINED BMD. | 623630 | 16:09:03 | 202216:09:03 | SUBJECT:REVIEW OF LMI “BOILER THERMAL EXPANSION INDICATBORS | AND THEIR USE ” O | DATE: 24.11.2022 | SUBJECT: REVIEW OF LMI “BOILER THERMAL EXPANSION INDICATORS AND THEIR USE ” | THE ABOVE APPROVED LMI WAS REVISED IN MONTH OF AUG ’2021. THE ENVISAGED CHANGES IN LMI ARE | ISSUE1; REV.8.00; NOV ’2022 HAS BEEN | THIS LMNI WITH DOC REF NO LMI | 006. | REVIEWED AND CHANGES ARE INCORPORATED AS ENVISAGED IN OGN REF DOC: COSISO00OGN | MAY PLEASE ACCORD APPROVAL FOR THIS REVISED VERSION OF LMI. | 16:49:05 | FOLLOWINNG CHANGES INCORPORATED IN REVISED LMI AT PAGE 3 OF 10: | ADDITIONAL FREAQUENCY OF READINGS ADDED DURING START UP TO FULL LOAD AFTER MODIFICATION AND LONG SHUT | DOWN OF UNIT. | 11:33:45 | 09:33:34 | 11:01:37 | 11:46:30 | 12:29:20 | 202216:03:28 | 16:03:28 | ISSUE NO.1; REVISION NO. 8.00; DATE: NOV ’2022 | BOILER THERMAL EXPANSION | INDICATORS AND THEIR USE | 1.0 TITLE OF LMI BOILER THERMAL EXPANSION | INDICATORS | DATE ISSUE1; REV.8.00; NOV ’2022 | 4.PREPARED BY: SR. MGR. | GM MTC. SIGNATURE | 8. REVIEWED AND APPROVED BY | 10.INDEX LIST ENCLOSED. | TITLE: BOILER THERMAL EXPANSION INDICATORS REV: 8.00 | DATE: NOV’2022 | PAGE : 1 OF 10 | 7.0 METOLOGY OF 3 | 12.0 REVISION INDEX 56 | 13.0 DISTRIBUTION LIST 7 | 14.0 COMPLIANCE RECORD 8 | 15.0 EXPANSION SURVEY RECORD 910 | PAGE : 2 OF 10 | THE TWOPASS DRUM TYPE BOILER INSTALLED AT SIMHADRI IS SUSPENDED FROM TOP AND | EXPANDS DOWNWARDS AS IT IS BEING BROUGHT UP TO PRESSURE AND TEMPERATURE. THE BOILER IS | PROVIDED WITH THERMAL EXPANSION INDICATORS AT DIFFERENT PREDETERMINED LOCATIONS TO | MEASURE | MONITOR AND RECORD THE EXPANSIONS AT DIFFERENT HOT CONDITIONS. | IF THE BOILER IS NOT ALLOWED TO EXPAND FREELY IT MAY LEAD TO FAILURE OF FURNACE TUBE | ATTACHMENTS TO BACKSTAY HOT CHANNEL AND BUCK STAY SLIDING CONNECTIONS. THIS COULD LEAD TO | PROLONGED OUTAGES. | THE PURPOSE OF BOILER EXPANSION INDICATORS IS NOT FOR ABSOLUTE ACCURACY BUT TO SEE | QUICKLY AND EASILY WHERE ANY MAJOR PROBLEMS IN BOILER MOVEMENT OR ANY INCONSISTENT | RELATIVE TO ANOTHER HAS OCCURRED. THE USE OF INDICATORS | MOVEMENTS OF ONE POSITION OR LEVEL | AT THE UPPER LEVEL IS PRIMARILY TO ENSURE THAT THE SUPPORTING SYSTEM IN THE ROOF DEAD SPACE | IS FUNCTIONING CORRECTLY AND NOT TRYING TO TWIST OR TILT THE BOILER AND THAT THE HORIZONTAL | ABSOLUTE ERRORS CAN | MOVEMENTS ARE NOT BEING AFFECTED BY THE INTERNAL PIPING. IN THIS AREA | BE SMALL BUT SIGNIFICANT ON A PERCENTAGE BASIS. THE BOTTOM LEVEL INDICATORS ARE INTENDED TO | SHOW THE EFFECT OF ANY MAJOR RESTRICTIONS TO VERTICAL MOVEMENTS AND ANY UNDUE FORCES | ACTING ON THE BOTTOM ERS FROM THE FEED PIPING. INDICATORS AT INTERMEDIATE LEVELS ARE | INTENDED PRINCIPALLY TO QUICKLY ISOLATE THE AREA WHERE A RESTRICTION IS OCCURRING AND TO SEE | THE EFFECTS OF RESTRICTIONS OCCURRING AT OTHER LEVELS. INDICATORS ON DRUM | DOWN COMERS AND | ERS ARE TO ENSURE CORRECT SUPPORT | FREEDOM FROM ROTATIONAL STRESSES ON STUB WELDS AND | THE CORRECT RETURN TO DATUM. | THE OBJECTIVE OF THIS LMI IS TO ESTABLISH A SYSTEM OF PERIODIC EXAMINATION | AND RECORDING OF BOILER EXPANSION MOVEMENTS. | PERIODIC RECORDING OF EXPANSION MOVEMENTS. IT REFERS ESSENTIALLY TO THE MEASUREMENT OF | BOILER CASING AND STEEL MOVEMENT. | BOILER THERMAL EXPANSION INDICATORS REV: 5.00 DATE: JAN’2020 | PAGE : 3 OF 10 | A INTEGRITY OF EXPANSION INDICATORS AT PREDETERMINED LOCATIONS IS TO BE ENSURED. | B REGULAR INSPECTION TO ENSURE FREE EXPANSION OF BOILER. | C MEASUREMENT AND RECORDING OF BOILER EXPANSION MOVEMENTS AT DIFFERENT HOT | CONDITIONS. | D EXCEPTION RECORDING AND TAKING UP WITH MANUFACTURER | ERECTOR. | AND NECESSARY REMEDIAL ACTION IS TO BE TAKEN TO ENSURE PRESENCE AND FUNCTIONAL UTILITY OF | STATIC POINTER AND MOVABLE SCALE ATTACHED TO THE BOILER. DATUM CHECKING AND CORRECTION | ATTACHED TO THE BOILER | BEFORE AND AFTER THE BOILER IS FILLED | DURING LIGHT UP AND BOILING OUT PERIODS | IF REQUIRED | DURING STEAM PURGING | ACID CLEANING TIME | STARTUP | DURING SAFETY VALVE PRESSURE SETTING | TO FULL LOAD AFTER MODIFICATIONS AND SHUTDOWN. | FREQUENCY : DURING OVERHAUL | B VISUAL INSPECTION OF BOILER AT SIX MONTHLY INTERVALS AND AFTER EVERY OVERHAUL AT ALL | BEAM | SUPPORT IS FOULING WITH THE PRESSURE | ELEVATIONS TO ENSURE THAT NO RIGID STRUCTURE | PART COMPONENTS. | FREQUENCY : EVERY SIX MONTHS | C AFTER EVERY OVERHAUL THE BOILER EXPANSION MOVEMENTS ARE TO BE RECORDED DURING THE | FIRST LIGHT AFTER OVERHAUL AT THE FOLLOWING PRESSURE | TEMPERATURE INTERVALS | INTERVAL DRUM SATURATION TEMP | PRESSUREBAR DEG. CENTIGRADE | DEG. CENTIGRADE | BAR | 01 10 180 | 02 40 250 | 03 150 343 | FREQUENCY : AFTER OVERHAUL | D IF ANY ASH ACCUMULATIONS ARE THERE SAME ARE TO BE RECORDED ALONG WITH EXPANSION | NEGATIVE SLOPE AND FG DUCT EXPANSIONS. | READINGS OF BOILER HORIZONTAL DUCT POSITIVE | E EXCEPTION RECORDING AND REPORTING TO MANUFACTURER BMD | DATE: NOV ’2022 | PAGE : 4 OF 10 | THE EXCEPTIONS ENCOUNTERED DURING INSPECTION AS COMPARED TO ERECTION PROTOCOLS ARE TO BE | REPORTED AS PER THE FOLLOWING FORMAT AND TO BE TAKEN UP WITH MANUFACTURER | BMD. | OF BOILER EXPANSION INDICATORS AS DETAILED IN THE LMI ARE WITH PRESSURE | B REPORTS OF EXPANSION SURVEY CARRIED OUT | THE ABOVE RECORDS ARE TO BE MAINTAINED BY AREA ENGINEER PR. PARTS GROUP. | THIS DOCUMENT SHALL BE REVIEWED BY OF THE PROJECT ON TWOYEARLY BASIS. | 201521 | 10:22:44 | 202310:22:44 | SUBJECT:APPROVAL OF LMI ON GUIDELINES FOR INSPECTION AND | CONCRETE STRUCTURES LMI NO. LMI | LMI REFERENCES: | 007 REV.2 | MAY 2023: COPY ENCLOSED | REVISED IN MAY 2023 | THE SUBJECT LMI HAS BEEN REVIEWED AND REVISED | BASED ON THE ABOVE MENTIONED OGN REVISED IN MAY 2023 | REV 8 | ACCORDINGLY REV 8. | REVISION NO 2 OF COSISO00OGN | 007 AND SUBMITTED FOR APPROVAL PL. | 11:06:04 | 18:05:51 | 18:00:58 | 11:13:28 | 17:21:22 | 09:28:13 | 16:22:56 | 18:41:33 | नीलांजन मंड़़ल अपर महाप्रबंधक | 16:07:04 | MAY BEN APPROVED. | 16:45:20 | िवश्व मोहन चौधरी महाप्रबंधक | 17:31:39 | 18:31:25 | 16:15:23 | 16:17:34 | 08:36:03 | 19:56:56 | 09:20:09 | AND CONCRETE STRUCTURES | NONCORROSIVE ATMOSPHERE | NON-CORROSIVE ATMOSPHERE | 611938 | D20 | 22:58:03 | 202222:58:03 | SYSTEMS” O | DATE: 20.11.2022 | 016 | 016" CIRCULATED BY CCOS. THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER | PUT UP FOR APPROVAL PLEASE | THE SUBNJECT LMI WITH DOC REF LMI | ISSUE1; REV.5.00; NOV’2022 HAS BEEN | REVISED AFTER INCORPORATING CHANGES AS PER OGN DOC WITH REF COSISO00OGN | 016. | 19:00:44 | 1.REVISNION DONE AS PER CLAUSE 5.4.2 AND 5.8.5 OF NRE OGN | 2. ANNEXURE 1 CHECK LIST INCLUDED IN REVISED LMI | REVISED LMI ATTACHED DOC NEW LMI MAY PLEASE BE APPROVED. | ATTACHED DOC NEW LMI | 09:11:47 | 09:35:08 | NEW LMNI REVISED MAY PLEASE BE ACCORDED APPROVAL. | 11:12:09 | 11:52:08 | 12:24:58 | BOILER SUPPORT SYSTEMS | OF BOILER SUPPORT SYSTEMS | DATE ISSUE1; REV.5.00; NOV’2022 | REV. NO. : 1 JUNE 2020 | PP S I G NATURE_______________ | AGM BMD S I G N A TURE_______________ | SYSTEMS REV: 5.00 DATE: NOV’2022 | 10.0 RECORD KEEPING 5 | 11.0 REVIEW 5 | 12.0 REVISION INDEX 6 | THE TWOPASS DRUM TYPE BOILERS AT SIMHADRI ARE HUNG FROM THE TOP MAIN SUSPENSION STEEL | WORK SUPPORTED BY THE MAIN BOILER HOUSE COLUMNS. DRUMS ARE SUPPORTED BY TIE RODS HUNG | FROM THE TOP MAIN SUSPENSION STEEL WORK. THE MAIN BOILER WALLS ARE HUNG FROM THE TOP | STEEL WORK. THE RADIANT | CONVECTION TUBE BANK ASSEMBLIES TOGETHER WITH THE ROOF TUBES | ARE ALSO HUNG VIA INTERMEDIATE BEAM ASSEMBLIES FROM THE TOP MAIN STEEL WORK. | ECONOMIZERS ARE SUPPORTED FROM TOP MAIN STEEL WORK | ALSO BY BEAMS WHICH SPAN IN THE | REAR WALLS. AT THE TOP OF THE BOILER | THE BOILER INNER | GAS PASSES BETWEEN ENCLOSURE FRONT | ALL RISER PIPES | CASING FORMS A CANOPY ROOF ENCLOSING THE BOILER DRUM | ERS | THE INTER | TUBING ABOVE THE FURNACE AND ENCLOSURE ROOF TUBES CALLED DEAD SPACE. | STAGE PIPE WORKS | THE FURNACE AND ENCLOSURE ROOF TUBES ARE COVERED WITH A REFRACTORY LAYER | PLATE WORK | AND THIS FORMS THE PRIMARY SEAL BETWEEN GAS AND DEAD SPACE. ALL THE BOILER SUPPORTS | WHERE THEY ARE SUBJECTED TO LOADING AND | NECESSARILY PASSTHROUGH BOILER TOP DEAD SPACE | TEMPERATURE. SUPPORT STRUCTURES ARE ALSO LOCATED IN FURNACE NOSE AND BOTTOM DEAD SPACES. | THE OBJECTIVE OF THIS LMI IS TO MAINTAIN THE INTEGRITY OF BOILER SUPPORT STRUCTURES LOCATED | IN DEAD SPACES. | OF STRUCTURAL INTEGRITY OF BOILER SUPPORT STRUCTURES. IT REFERS ESSENTIALLY TO THE TOP MAIN | STEEL SUSPENSION STEEL WORK AND THE ASSOCIATED BOILER SUPPORT COMPONENTS AND | ATTACHMENTS LOCATED IN THE TOP DEAD SPACE. | DATE: APR’2013 | SYSTEMS REV: 5.00 DATE:NOV’2022 | TO ACHIEVE THE OBJECTIVE OF THIS LMI THE FOLLOWING APPROACH IS TO BE FOLLOWED : | A REGULAR MONITORING OF DEAD SPACE DUST LEVELS. | B REGULAR REMOVAL OF DEAD SPACE DUST ACCUMULATIONS. | C CONTROL OF DEAD SPACE DUST INGRESS | D PERIODIC INSPECTION OF DEAD SPACE SUPPORT COMPONENTS AND NECESSARY PREVENTIVE | ACTIONS. | TOP DEAD SPACE AND FURNACE NOSE DEAD SPACE | A INSPECTION OF BOILER DEAD SPACE TOP DEAD SPACE AND FURNACE NOSE DEAD SPACE TO | MONITOR THE DUST LEVELS DURING SHUTDOWNS OF THE UNITS FOR A TIME GREATER THAN 48 | FREQUENCY – DURING UNIT BREAKDOWNS. | B REMOVAL OF BOILER DEAD SPACE DUST ACCUMULATIONS WITH PROPER SAFETY PRECAUTIONS | AND APPLICATION OF FLEXIBLE SOFT SEALING COMPOUNDS IN MORE DEFECT PRONE | FREQUENCY – DURING SHUTDOWNS AS PER NEED BASIS. | C DUST LEVEL SURVEY TO BE CARRIED OUT AT THE BEGINNING OF OVERHAUL TO DETERMINE LOCAL | SEAL DETERIORATION AND FOR POSSIBLE PRESENCE OF FURNACE ROOF BURN HOLES. AMOUNT OF | TO BE WEIGHED AND TO BE | DUST COLLECTED FROM DEAD SPACE DURING OVERHAUL CLEANUP | LOGGED ALONG WITH BOILER RUNNING HOURS SINCE LAST CLEAN UP ACTION. | .PP | FREQUENCY DURING OVERHAUL | D INSPECTION OF ROOF SEAL PLATE WORK AND REFRACTORY AND REPAIR WORK AS NECESSARY. | E INSPECTION OF BOILER SUPPORT COMPONENTS AS DETAILED BELOW AFTER DUST CLEARANCE OF | BOTTOM AND NOSE | LOOSENESS. IF THE LOWER END | DEAD SPACE BOTTOM AND NOSE FOR STRUCTURAL INTEGRITY | OF A ROD IS HIDDEN IN LAGGING | LAGGING MAY BE REMOVED TO CHECK THE CONNECTION. | I. INSIDE DEAD SPACE | A DRUM STRAPS | B SUPPORTS OF PIPE WORK ASSOCIATED WITH DRUM | C MAIN BOILER WALL SUPPORTS | D RADIANT AND CONVECTIVE TUBE BANK SUPPORTS | PAGE : 4 OF 8 | MAINSTREAM AND HOT REHEAT LINE SUPPORTS | E ERS | F FURNACE AND ENCLOSURE ROOF SEALS RADIANT AND CONVECTIVE TUBE BANK | PENETRATIONS | G ROOF TUBE SUPPORTS INCLUDING RANDOM SAMPLE OF ROOF TUBE CONNECTION LUGS | II. COMPONENTS AT CANOPY ROOF LEVEL | STEEL WORK | A CANOPY ROOF PLATE WORK | B SUPPORT CONNECTIONS TO CANOPY ROOF PLATE WORK | C SEAL POTS WHERE SLING RODS PASS THROUGH CANOPY ROOF | III. COMPONENTS ABOVE CANOPY ROOF | A PARTS OF SLING LINE ABOVE CANOPY ROOF | INCLUDING CONNECTIONS TO TOP MAIN | STEEL WORK FRAME | B TOP FRAME STEEL WORK | PACKER PLATE UNDER THE MAIN TIE ROD NUT. | C CONDITION OF WASHER | F INSPECTION OF SUPPORT SUSPENSION RODS FOR NECKING AND REDUCTION OF DIAMETER ON | ACCOUNT OF DEW POINT CORROSION DURING OVERHAUL. | REPAIR AND RECTIFICATION OF DEFECTS OBSERVED INCLUDING TIGHTENING OF LOOSE RODS TO | OEM. WHERE IT IS | BE DONE AFTER CONSULTATION WITH CORPORATE ENGINEERING | NECESSARY TO MEASURE THE EXISTING LOADS IN A SLING LINE | A CHECK WEIGHING MET | USING A SERIES OF HYDRAULIC JACKS DYNAMOMETERS MAY BE USED. IF THE TIE ROD | SUPPORT FRAME BOTTOM SIDE FITTED WITH LOCK NUT THE SAME SHOULD HAVE GAP FROM THE | STRUCTURE TO ENSURE CONTRACTION DURING COOLING. | MANUFACTURER | FORMAT AND TO BE TAKEN UP WITH CORPORATE ENGINEERING | DESCRIPTION OF UNIT NO. LOCATION OF REMARKS | EXCEPTION EXCEPTION | 608694 | 17:36:03 | 202217:36:03 | SUBJECT:REVIEW OF LMI “BOILER ER LIGAMENT CRACKINGB – | HYDRAULIC LEAK TESTING DURING BREAKDOWN REOPAIRS | DATE: 18.11.2022 | SUBJECT: REVIEW OF LMI “BOILER ER LIGAMENT CRACKING – HYDRAULIC LEAK | TESTING DURING BREAKDOWN REPAIRS” | 005" CIRCULATED BY CCOS. THE ENVISAGED CHANGES IN LMI ARE INCORPORATED AS PER | AS PER REFERENCE | MAY PLENASE PROVIDE APPROVAL FOR THE REVISED VERSION OF SUBJECT LMI DOCUMENT WITH REV6 | 19:56:06 | THE NECNESSARY CHANGES DONE I.E. | 1. TEMPERATURE MEASUREMENT CLAUSE ADDED | 2. CYCLIC HYDRO CALUSE REVISED AND GRAPH INCLUDED. | REVISED LMI ATTACHED AS ANNEXURE MAY PL. BE APPROVED | ATTACHED AS ANNEXURE | 11:06:13 | 13:50:53 | 13:24:51 | PLEASE RNEVIEW THE DOCUMENT. | 12:03:37 | 12:08:56 | 17:03:52 | राजेश गणपतराव मोिह्दकर उप महाप्रबंधक | RAJESH GANPATRAO MOHADIKAR 009153 DY. GENERAL MANAGER | 9650992656 | RAJESHMOHADIKAR@NTPC.CO.IN | 11:42:17 | BEING FNOLLOWED .FORWARDED FOR FURTHER APPROVAL | 17:07:36 | 19:46:12 | 18:50:24 | 19:24:22 | ISSUE NO.1; REVISION NO. 6.00; DATE: NOV’2022 | BOILER HYDRAULIC LEAK | TESTING DURING BREAKDOWN | REPAIRS | 1.0 TITLE OF LMI TEST DURING BREAKDOWN | DATE ISSUE1; REV.6.00; NOV’2022 | REV.NO.1 | 9.DISTRIBUTION LIST ENCLOSED | TITLE: BOILER HYDRAULIC LEAK TEST DURING BREAKDOWN | REPAIRS REV: 6.00 DATE: NOV’2022 | TUBE LEAK OR TO CONFIRM THAT ALL DAMAGED AREAS HAVE BEEN REPAIRED. HOWEVER | DURING THIS TIME | THE ERS ARE LIKELY TO BE STILL HOT AND THERE IS A RISK OF THERMAL SHOCK AND CONSEQUENT CRACK | IT IS NECESSARY TO ENSURE THAT | GENERATION AND PROPAGATION. TO MINIMIZE THE RISK OF DAMAGE | ER METAL TEMPERATURES ARE NOT QUENCHED BY MORE THAN 50C BUT UNITS WITHOUT LIGAMENT | CRACKS QUENCHING CAN BE MAXIMUM UP TO 100C.CYCLIC HYDRO AT WATER TEMPERATURE LESS | THAN 50C IS TO BE DONE FOR BOILERS OPERATING UNDER FLEXIBLE REGIME. ADDITIONAL | TEMPERATURE MONITORING IS TO BE ENSURED. | CARRYING OUT HYDRAULIC LEAK TEST OF BOILERS | TO PREVENT BOILER ER LIGAMENT CRACKING. | STEPS TO BE FOLLOWED AND | THE SCOPE OF THIS LMI IS TO DETAIL THE PARAMETERS TO BE MONITORED | CONSTRAINTS THAT ARE TO BE RIGIDLY ADHERED TO WHILE CARRYING HYDRAULIC LEAK TEST OF ALL FOSSIL | BOILERS. | 005 REV.NO.1 CIRCULATED BY | • BOILER ER LIGAMENT CRACKING – HYDRAULIC LEAK TEST | DURING BREAKDOWN REPAIRS REV: 4.00 DATE: MAR'2020 | 6.0 SPECIFIC INSTUCTIONS | THE OBJECTIVE OF THE LMI IS SOUGHT TO BE ACHIEVED THROUGH: | • EXTENDING BOILER COOLING TIMES OR WATER FILLING TIMES TO AVOID THERMAL SHOCK CAUSED | BY SUDDEN QUENCHING IN SUPER HEATER ERS. | • CARRYING OUT SPECIFIC ACTIONS IN SEQUENCE AT DIFFERENT STAGES OF INSERVICE HYDRAULIC | PRESSURE TESTING OF BOILERS | PT PLANT | 699453 | 17:52:42 | 202417:52:42 | SUBJECT:PERFORMANCE OPTIMIZATION OF P.T. PLANT CHLORINATION SYSTEM AND | CLO2 | ALL THE NRELEVANT CHANGES ARE INCORPORATED IN THE LMI BASED ON THE ORIGINAL OGN. RECORD OF REVESION IS ALSO | INCLUDED IN THE LMI. | 09:32:36 | 18:42:53 | 14:31:17 | POINT NON 9 MAY PLEASE BE REVIEWED | 16:41:37 | 18:10:21 | 17:17:45 | POINT NON. 9 REVISED ACCORDINGLY | 17:15:34 | REVISEDN LMI IS ATTACHED. | 21:37:11 | I RESPONSIBILTIES | REVIEWNED AND FOUND IN ORDER W.R.T C | 16:43:47 | 17:02:10 | 19:44:26 | 17:58:51 | THE LMNI IS REVIEWED BY ALL RELATED S AND NECESSARY INPUTS ARE INCORPORATED. | SUBMITTED FOR FINAL APPROVAL PLEASE. | 18:18:49 | 20:01:28 | 18:20:54 | 18:21:54 | PAGE 1 OF 27 | 16:24:46 | 202516:24:46 | 226235 IDATE:13 | SIMHADRI LMI | 015 IS REVISED IN LINE WITH THE NEW OGN. | JAN2023 ISSUE 04 | ISSUE 04 | JUNE2025 | OGN ARE ATTACHED. | CHANGES IN LMI ARE BRIEFED IN THE BELOW TABLE. LMI | SL.NO. CODE OF PRACTICES MODIFICATION | 1. SEC 4.1GENERAL GUIDELINES NEW POINTS INCORPORATED. | FILTER WATER NEW PARAMETERS INCORPORATED. | CLARIFIED WATER | 3. SEC 5.1RW | 4. SEC 5.2 ON RESINBASED DM PLANT NEWLY INCORPORATED. | 5. SEC 5.2 TABLES 3A | 3C NEWLY INCORPORATED. | BASED DM PLANT | SEC 5.7 TABLE 6B SPECIFIC CHEMICAL MODIFIED FOR CALCULATION OF EXISTING IONIC LOADBASED | CONSUMPTION DATA FOR DM PLANT SPECIFIC CHEMICAL CONSUMPTION | SEC 6.0 | TABLE 8CMAIN PLANT | 8. FOOT NOTES MODIFIED. | PARAMETERS TO BE TESTED | 9. SEC 8.0 | TABLE 9A | 9BCOAL ANALYSIS FOOT NOTES MODIFIED. | GYPSUM ANALYSIS FOR | SEC 9.0 LIMESTONE | 10. NEWLY INCORPORATED. | MILL HYDRAULIC OIL MONITORING ADDED. CHP OIL | TABLE 10B | SEC 10.0B | 10C LUBE OIL | 11. FREQUENCY MODIFIED. ONE OIL ADDED IN GEAR BOX OIL | ANALYSIS | SECTION. FOOT NOTES MODIFIED. | 12. SEC 10.0CDGA FOOT NOTES MODIFIED. | TABLE 13AONLINE INSTRUMENTS MODIFIED. | 13. SEC 13.0 | TABLE 14A EQUIPMENT | SEC 14.0 | FOOT | MODIFIED FOR CHECKS TO BE DONE AND FREQUENCY | 14. | NOTES MODIFIED. | TABLE 14COVERHAULING JOBS | 15. DESCRIPTION AND RESPONSIBILITIES MODIFIED. | ANNEXUREII CLARIFIED WATER AND DM | 16. NEWLY INCORPORATED. | WATER COST CALCULATION TEMPLATE | देवेश कुमार प्रबंधक रसायन | DEVESHKUMAR@NTPC.CO.IN | 8005489020 | 226235 | COMPETENT AUTHORITY FOR IMPLEMENTATION AT NTPC SIMHADRI. | 16:59:04 | 16:49:09 | 17:04:04 | FOLLOWINNG CORRECTIONS ARE REQUIRED | 1.CHECKLIST SHOULD BE KEPT IN LAST PART OF LM AS ANNEXURES | 2.LAST 3 PAGES FORMATING AS PER STANDARD FORMAT TO BE DONE. | 3. LMI NO. SHOULD NOT CONTAIN ISUE 04 | IT IS TO BE CORRECTED AT EACH PAGE. | 10:08:11 | CORRECTNIONS ARE DONE AND DRAFT LMI ATTACHED. | 16:39:36 | 18:35:00 | 16:39:40 | 17:06:42 | LMI RENVIEWED | 12:19:03 | 16:47:43 | हमे न्त सैनी उप महाप्रबंधक | HEMANT SAINI 100407 DY. GENERAL MANAGER | 12:54:22 | 16:31:42 | 09:10:45 | 09:52:08 | 17:56:53 | 952310 | FUEL HAND. | LMIRIM | 202316:42:13 | 16:42:13 | HANDLING PLANT O | SUB: LMI 2023 “RELIABILITY IMPROVEMENT MATRIX OF COAL HANDLING PLANT” | PREPARED W.R.T CCOS ISSUED OGN | CCOS HAS ISSUED THE OGN COSISO00OGN | 057 | REV. NO.: 0 JAN 2023 “RELIABILITY | IMPROVEMENT MATRIX OF COAL HANDLING PLANT” COPY ATTACHED FOR READY REFERENCE. | COPY ATTACHED FOR READY REFERENCE | THE SAME HAS BEEN REVIEWED AND IN LINE WITH THE OGN | REF NO ” LMI | “RELIABILITY IMPROVEMENT MATRIX OF COAL HANDLING PLANT” HAS BEEN PREPARED AND IS | BEING PUT UP FOR REVIEW AND KIND APPROVAL PLEASE. | ग़ौव्ड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ॅऍस्ः वाण्ड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़्ड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ाण्ग़ी विरष्ठ प्रबंधक | GOWREESH VANDRANGI 009514 SENIOR MANAGER | GOWREESHVANDRANGI@NTPC.CO.IN | 8985574086 | HANDLING PLANT.PDF HAS BEEN REVIEWED AND FOUND IN LINE WITH OGN:COSISO00OGN | 057. | आशीष वमार् उप महाप्रबंधक | ASHISH VERMA 008140 DY. GENERAL MANAGER | ASHISHVERMA@NTPC.CO.IN | 9650995131 | 16:48:06 | REVIEWNED WITH REFERENCE TO OGN:COSISO00OGN | FOUND IN ORDER. SUBMITTED FOR | APPROVAL PLEASE. | वी श्रीिनवास राव उप महाप्रबंधक | VASAMSETTY SRINIVASA RAO 008155 DY. GENERAL MANAGER | FUEL HANDLING | VSRINIVASARAO01@NTPC.CO.IN | 9494198667 | 18:11:51 | 13:07:32 | 16:25:30 | FOUND IN ORDER. SUBMITTED FOR APPROVAL PLEASE. | 17:03:11 | 17:11:00 | 16:32:04 | 11:21:04 | 15:00:16 | 17:43:26 | 19:57:43 | REVISION NO.0 | DATE: MAR’2023 | ISSUE NO.1 | REF: COS-ISO-00-OGN | REF: COSISO00OGN | 057 REV. NO.: 0 JAN 2023 | RELIABILITY IMPROVEMENT MATRIX OF | COAL HANDLING PLANT | ............................................................................... | DATE: .................... | COAL HANDLING PLANT – FUEL MANAGEMENT | LMI: RELIABILITY IMPROVEMENT MATRIX OF COAL HANDLING PLANT | ISSUE NO. 1 REVISION : 00 DATE: | RELIABILITY IMPROVEMENT MATRIX OF COAL HANDLING PLANT | GOWREESH.V SR. MANAGER CHPO | ASHISH VERMA DGM CHPO | V SRINIVASA RAO DGM CHPM | NIRAJ KUMAR AGM CHPM | AGM FC | AMULYA KUMAR BEHERA | A. R. KOTESWARA RAO AGM CHPO | SANJIT MAJUMDAR AGM FM | REVIEWED BY VISHWA MOHAN CHOUDHARY GM FM | 1.1. SUPERSEDED DOCUMENT ................................................................................................................... 2 | 1.2. SCOPE .............................................................................................................................................. 2 | 1.3. REVIEW ............................................................................................................................................ 2 | 2.0 INTRODUCTION...................................................................................................................... 2 | 3.0 PROCESS ..................................................................................................................................... 2 | 3.1. FREQUENCY OF CAPTURING RIM DATA ...................................................................................... 2 | 3.2. UTILIZATION OF RIM MARKS ................................................................................................................. 2 | 4.0 RECORDS TO BE MAINTAINED ................................................................................................ 3 | 057 REV.0.0 | REV. 0 OCT. 2020 | 075 | 1.1. SUPERSEDED DOCUMENT OIN | RELIABILITY IMPROVEMENT MATRIX IS A BASIS FOR EVALUATION OF PERFORMANCE OF | 1.2. SCOPE | CHP. | REVIEW 2 YEARLY BASIS | OR AS AND WHEN REQUIRED | 1.3. REVIEW FREQUENCY LOWER | HENCE ITS RELIABILITY | COAL HANDLING PLANT PLAYS AN IMPORTANT ROLE IN STEADY GENERATION OF POWER | IS VERY IMPORTANT. | CHP RELIABILITY IMPROVEMENT MATRIX RIM HELPS IN IMPROVING THE RELIABILITY OF CHP EQUIPMENT | RIM | AND SYSTEMS BY MONITORING CRITICAL PERFORMANCE PARAMETERS. THE COMPLIANCE OF THIS MATRIX IS | USED AS BASIS FOR EVALUATION OF PERFORMANCE OF CHP OF ALL STATIONS. ACCORDINGLY | WEIGHTAGES | HAVE BEEN ALLOCATED TO RESPECTIVE PARAMETER FOR EVALUATION. IT ALSO ENABLES INTERNAL | BENCHMARKING AMONG CHP OF ALL STATIONS. | MONITORING OF MORE | IN ORDER TO INCORPORATE CHANGES ARISES WITH DUE COURSE OF TIME | AS WELL AS FOR POST FAILURE ANALYSIS A NEW VERSION OF RIM IS INTRODUCED. | 3.0 PROCESS | 3.1 FREQUENCY OF CAPTURING RIM DATA | M. DATA | WHICH SHOULD BE REVIEWED BY OF O | RIM MARKING TO BE DONE BY FM MONTHLY | TO BE RECORDED EVERY MONTH AND TO BE ENDORSED BY REGIONAL OS DURING ORT VISIT. DATA RECORDING | ENTERING IS DONE EITHER ON ONLINE PLATFORM OR MANUALLY THROUGH EXCEL SHEET AND SHOULD BE SENT TO COS | MONTHLY BY 7TH OF EACH MONTH | BY FM . | 3.2 UTILIZATION OF RIM MARKS | FOR THE CHP. | RIM MARKS IS USED AS PEM MARKS IN TOTALITY IN THE SCALE OF 3 | 4.0 RECORDS TO BE MAINTAINED | RELIABILTY IMPROVEMENT MATRIX OF COAL HANDLING PLANT | STATION: REGION: YEAR: MONTH: | ITEM FREQ REFERENCE WEIGHT | CRITERIA SL. NO EVALUATION CRITERIA RATING | DESCRIPTION UENCY DOCUMENTS AGE | A SAFETY SAFETY SAFETY IF ANY REPORTABLE | REPORT INCIDENT IN MONTH THEN | ENTIRE MARKS ON SAFETY | ELSE RATING ON | IS ZERO | DIFFERENT PARAMETERS | BELOW AS A1 TO A8 | 1 DEVIATION IN MONT SAFETY IF NO DEVIATION THEN FULL | 1.5 | PTW SYSTEM HLY REPORT MARKS ELSE 0 | 2 % CLOSURE OF MONT SAP REPORT 100% CLOSURE THEN FULL | 9990% CLOSURE | SAFETY DEVIATION HLY MARKS | 8970% 1.5 | THEN 1 MARKS | CLOSURE THEN 0.5 MARKS | ELSE 0 | 3 COMPLIANCE TO HALF SAP REPORT 100% COMPLIANCE THEN | SAFETY AUDIT YEARLY FULL MARKS | 9990% | OBSERVATIONS COMPLIANCE THEN 1 | 70% COMPLIANCE | MARKS | THEN 0.5 MARKS | 4 USE OF LOTO KIT IF 100% COMPLIED THEN | ISOLATION. | 5 JSA LINKED WITH PTW WITH IF 100% COMPLIED THEN | 1.0 | PTW JSA FULL MARKS ELSE 0 | 6 LOAD TESTING OF YEARLY IF 100% COMPLIED THEN | SAFET FULL MARKS ELSE 0 | LIFTING TOOLS | HOISTS | TACKLES | Y REPORT | LIFTS | 7 AVAILABILITY | IF 100% COMPLIED THEN | USE OF SAFETY REPORT FULL MARKS ELSE 0 | NET ALONG WITH | SAFETY KIT E.G. | FULL BODY | LIFE LINE | HARNESS | ROPE GRAB | FALL | ARRESTOR FOR | WORKING AT HEIGHT. | DUCT | 847230 IDATE:23 | 202418:44:31 | 18:44:31 | SUBJECT:LMI FOR DUCT | THE LMI FOR "DUCT | 059 IS BEING PUT FORWARD FOR APPROVAL. | 847230 | MAY PLZN APPROVED. | 19:01:51 | A NEW NLMI "DUCT | 059. | 00OGN | APPROVAL MAY KINDLY BE ACCORDED. | 12:01:00 | 16:49:29 | 11:27:47 | 11:48:17 | 059. FORMAT REVISED. | 10:52:15 | MAY PLZN APPROVE. | 11:35:32 | 15:47:41 | 10:46:53 | 09:44:23 | 09:10:27 | 17:13:54 | 07:10:49 | 059 | REVISION 0 | GUIDELINES FOR DUCT | REV.NO.:0 DATE: JANUARY 2024 | APPROVED FOR IMPLEMENTATION BY: | HOP NTPCSIMHADRI | NTPC-SIMHADRI | JANUARY 2024. | 1 TITLE OF LMI GUIDELINES FOR DUCT | EXPANSION JOINT | DATE REVISION 0 | REV. NO.: 0 DEC 2023 | MGR. BMD | 4 PREPARED BY: SAMRAT BANIK | 5 CHECKED BY: RITESH KUMAR | 6 CHECKED BY OM PRAKASH | 7 CHECKED BY U. S. VERMA | 8 CHECKED BY T. KANUNGO | AGMSAFETY | 9 RECHECKED BY MATHEW EIPE KOVOOR | 10 REVIEWED BY: D. P. PATRA | HOPNTPCSIMHADRI | 11 APPROVED BY SANJAY KUMAR SINHA | 12 DISTRIBUTION LIST ENCLOSED. | SL NO CONTENTS PAGE NO. | 2.0 INTRODUCTION 1 | 4.0 SAFETY ASPECTS 1 | 6.2 INSPECTION | 6.3 GENERAL GUIDELINES 4 | 7.0 APPENDIX1 CHECKLIST 5 | MGR | 977333 IDATE:08 | LMI_OHE | 202412:39:47 | 12:39:47 | SUBJECT:LMI FOR SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTIONO. | SUB: APPROVAL OF LMI FOR 'SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION' | 058 IS HERE | THE LMI FOR SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION WITH REF NO: LMI | BY PUT UP FOR APPROVAL OF COMPETENT AUTHORITY. | ENCLOSURES: | REF NO: LMI | 01.LMI FOR SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION | 058 REV. NO.: 0 NOV. 2023 | 02.OGN COSISO00OGN | नरिसहुलु नीलपु उप महाप्रबंधक | NARISIMHULU NEELAPU 008049 DY. GENERAL MANAGER | 9491160670 | NNARISIMHULU@NTPC.CO.IN | 977333 | 13:10:09 | 15:15:37 | 16:05:51 | 16:33:08 | 17:46:37 | 17:57:11 | 14:58:55 | 19:04:02 | REV. NO.: 0 NOV. 2023 | LMI – SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION | CONTROLLED COPY | N T P C L I M I T E D | LOCAL MANAGEMENT INSTRUCTION – LMI | REVISION: 00 DT: _____ | _____ | SAFE WORK PRACTICES IN ELECTRIFIED | TRACK SECTION | APPROVED FOR IMPLEMENTATION BY SHRI S K SINHA | OF PROJECT SIMHADRI | ___ | DATE: ____ | PAGE 1 OF 21 | TITLE OF LMI: SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION | CHECKED | ISSUE REVISION PREPARED REVIEWED APPROVED | DATE CHANGES DONE | NO NO BY BY BY | ALL CLAUSES ARE NEW A K GM O | 2024 N. NARISMHULU HOP | 01 00 __ | AS THE DOCUMENT IS BEHERA | BEING ISSUED FOR THE OTHER | FIRST TIME. S | PAGE 2 OF 21 | ISSUE NO. : 1 REVISION: 0 DATE : . .2024 | REVIEW 02 YEARLY BASIS | FREQUENCY WHEN REQUIRED | LOWER. | NAME SHRI DESIGNATION SIGNATURE | PREPARED BY N NARISIMHULU DGM FT | AMULYA KUMAR BEHERA AGM FC | A R KOTESWAR RAO AGM FM I | FM I | TUSHAR KANUNGO AGM SAFETY | REVIEWED BY S.J.DAVID GENERAL MANAGER O | ISSUE BY SANJAY KUMAR SINHA CHIEF GENERAL MANAGER | ______ | DATE OF ISSUE _____ | PAGE 3 OF 21 | TABLE OF CONTENTS | SECTION SUBJECT PAGE NO | 1.0 INTRODUCTION 56 | 2.0 SUPERSEDED DOCUMENTS 6 | 2.1 REFERENCE DOCUMENTS 6 | 3.0 RECORDS OF REVISION 6 | 5.0 PROCESS 7 | 5.1 HAZARDS INVOLVED 7 | 5.2 GUIDELINES FOR OHE ISOLATION AND DISCHARGE 7 | 5.3 COMPETENCY CERTIFICATE 8 | 5.4 PRECAUTION DURING WORK 8 | WAGON UNDER ELECTRIFIED TRACK 8 | 5.5 WORK WHICH MAY REQUIRE CLIMBING ATOP LOCO | 7.0 S | 8.0 WORKS ON OTHER STRUCTURES NEAR OHE PRECAUTIONS 10 | 9.0 ASSOCIATED DOCUMENTS 11 | 9.1 ANNEXUREI: CHECK LIST EQUIPMENT AND RECORDS 12 | REMOVE TEMPORARY EARTH 1314 | 9.2 ANNEXUREII: STEPS TO PROVIDE | 9.3 ANNEXURE – III: SAFETY MEASURES FOR SAMPLING PERSONNEL 15 | 9.5 ANNEXURE – V: SAFETY MEASURES FOR S | WORK IN WAGON TIPPLER AREA 20 | 9.7 ANNEXURE – VII: SAMPLE – COMPETENCY CERTIFICATE 21 | WORK WHICH MAY REQUIRE CLIMBING ATOP LOCO | WAGON UNDER MGR CONTROL ROOM SHIFT | 9.3 IN CHARGE | MGR-O | ELECTRIFIED TRACK AS PER SECTION 5.5 | STEPS TO PROVIDE | REMOVE TEMPORARY EARTH AS PER SECTION 9.2 MGR CONTROL ROOM SHIFT | IN CHARGE | 9.5 ENGINEER | SECTION 7.0 | SECTION 8.0 ENGINEER | WORK IN WAGON TIPPLER AREA AS PER MGR CONTROL ROOM SHIFT | SECTION 9.6 IN CHARGE | ENSURING COMPETENCY CERTIFICATE AS PER SECTION 9.7 MGR | PAGE 4 OF 21 | FUEL MANAGEMENT ARRANGES COAL FROM THE LINKED MINES AND TRANSPORTS IT THROUGH INDIAN | RAILWAYS TO THE PLANT PREMISES. NTPCSIMHADRI RAILWAY SIDING IS THE LIFELINE OF THE SIMHADRI THERMAL | POWER PLANT. | NTPCSIMHADRI RAILWAY SIDING IS HAVING ABOUT 28 KM TRACK FOR SAFE COAL RAKE MOVEMENT FROM | JAGGAYYAPALEM TO THE UNLOADING POINT I.E. INSIDE PLANT PREMISES AND VICE VERSA. THERE IS SINGLE TRACK | D THERE ARE | D CABIN WITH A LOOP LINE AT DUVVADA RAILWAY STATION. FROM R | FROM JAGGAYYAPALEM TO R | ONE LOAD LINE TO TRACK HOPPER AND WAGON TIPPLERS AND OTHER INDEPENDENT EMPTY | TWO RAILWAY TRACKS | LINE HAVING LOOP LINE FOR OIL SIDING. ALSO | THE ELECTRIFICATION OF | TO FULFIL THE INCREASING POWER DEMAND | EXISTING SIDINGS WAS EXTENDED INSIDE YARD TO MEET THE COAL REQUIREMENTS AND TO REDUCE THE COAL | UNLOADING TIME. | THERE ARE | OHE | BOULDERS | OTHER ACTIVITIES LIKE COAL UNLOADING | REMOVAL OF STICKY COAL | REMOVAL OF TARPAULINS FROM | T WHICH IS CARRIED OUT AT NTPC SIMHADRI. | WITH THE ENTIRE TRACK BEING ELECTRIFIED | IT IS NECESSARY TO HAVE A GUIDELINE FOR ENSURING SAFETY WHILE | WORKING UNDER ELECTRIFIED TRACK. THE MAIN OBJECTIVE OF THESE INSTRUCTIONS IS TO PROVIDE SAFE WORK | ENVIRONMENT FOR ALL PERSONS UNDER ELECTRIFIED TRACK. | BRIEF DESCRIPTION OF AVAILABLE SYSTEMS: | 2001 | UNDER WALTAIRDIVISION OF | STATION STDV | NOTIFIED ON 14 | 12328677 NOTIFIED ON 14 | DIVISION | ALPHA | NUMERIC CODE E.CO.RAILWAY ZONE. | DVD | SERVING STATION DUVVADADVD | ALL COAL RAKE MOVEMENTS ARE DONE BY RAILWAY LOCOS AND THEIR CREW | NO OF LOCOMOTIVES NIL ALL COAL RAKE MOVEMENTS ARE DONE BY RAILWAY LOCOS AND THEIR CREW | NO OF WAGONS NIL ALL INCOMING COAL WAGONS BELONGS TO INDIAN RAILWAYS | ALL INCOMING COAL WAGONS BELONGS TO INDIAN RAILWAYS | TYPE OF WAGONS THAT | VARIOUS TYPES OF BOBRN AND BOXN WAGONS OF INDIAN RAILWAYS. | STATION CAN HANDLE | UNLOADING POINTS 02 NUMBERS OF TRACK HOPPERS. 02 NUMBERS OF WAGON TIPPLERS. | SCHEME OF WORKING OF | ENGINE ON LOAD | EOL ENGINE ON LOAD | TRAINS | 6O KG +52 KG RAILS ON 6OKG SLEEPERS | FAN SHAPED LAYOUT | TRACK LAYOUT | CROSSINGS. | CHARGEABLE DISTANCE | 23.94 KM | FROM DUVVADA | ONE FOR LOAD | OTHER FOR EMPTY. | OTHER FOR EMPTY | 02 LINES ONE FOR LOAD | CROSSING STATION YARD | PAGE 5 OF 21 | 07 LINES: ALL OHE LINES | O1 SICK LINE. | LINE NO: 1 | 2 FOR PARKING LOAD RAKES+ LIGHT ENGINES LINE NO: 3 FOR THROUGH | MOVEMENT OF LOADED RAKES. | RECEPTION | DESPATCH | LINE NO: 4 FOR THROUGH MOVEMENT OF EMPTY RAKES. | D YARD. | 7 FOR PARKING EMPTY RAKES + PILOT WAGONS. | LINE NO: 5 | ONE SICK LINE AVAILABLE FOR SICK WAGONS STABLING. | D YARD TO TRACK SINGLE LINE AVAILABLE WITH NECESSARY INTERCONNECTIONS | TURNOUTS WITH | AVAILABLE | 2 AND TO POINTS | CROSSINGS FOR MOVEMENT OF LOADED RAKES TO EITHER OF THE WAGON | HOPPER1 | WAGON TIPPLER1 | 2 TIPPLER. | FIVE MANNED LEVEL CROSSINGS FROM JAGGAYYAPALEM STATION TO NTPC IN | LEVEL CROSSINGS MOTION WEIGH BRIDGE AND 08 UNMANNED LEVEL CROSSINGS 08 NOS INSIDE | ENTIRE TRACK FROM TAKEOFF POINT IS AVAILABLE WITH OHE EXCEPT AT WTS | TABLE PORTIONS. | RELATED | WAGON TIPPLERS 1 | 2 ALONG WITH SIDE ARM CHARGERS | WAGON TIPPLERS | EQUIPMENT’S AVAILABLE. | ONE DEDICATED ENGINE PASSING LINE BETWEEN THE WT LINES AND TWO ENGINE | ENGINE ESCAPE LINES AT | ESCAPE LINES AT PRETIPPLING AND TWO ENGINE ESCAPE LINES AT POSTTIPPLING | EMPTY BULB AVAILABLE FROM ALL THS | WTS AND ENGINE LINE WITH OHE. | LOCO MOVEMENT AT ELECTRIC ENGINES MOVES OVER ENGINE ESCAPE LINES AND DIESEL ENGINES CAN | WAGON TIPPLERS MOVE OVER THE WAGON TIPPLER TABLE ALL THE TIME. | AVAILABLE WITH RRI SYSTEM HAVING 03ADVANCCE STARTERS | 06HOME SIGNALS | 43 MAIN SIGNAL | 14POST SHUNT SIGNALS | 36GROUND | 03 CALLING ON SIGNALS | SIGNALLING SYSTEM | 03 DERAILING SWITCHES | 108 TRACK | 64 POINTS AND CROSSINGS | SHUNT SIGNALS | 12AXLE COUNTERS. | CIRCUITS | TOKEN LESS COOPERATIVE BLOCK INSTRUMENTS AVAILABLE AT CROSSING STATION | BLOCK INSTRUMENTS | AND R | 2.0 SUPERSEDED DOCUMENTS – NIL | 2.1 REFERENCE DOCUMENT: SAFE WORK PRACTICES IN ELECTRIFIED TRACK SECTION: COSISO00 | 058 REV NO. 0 | ISSUED IN NOV 2023. | 3.0 RECORDS OF REVISION: NIL | S OF: S OF FM | PAGE 6 OF 21 | 989106 | 12:54:50 | 202412:54:50 | SUBJECT:APPROVAL OF NEW LMI “BOILER COOLING CUM PRESERVABTION | PROCEDURE” O | 059 GUIDELINES. | अश्वनी सचदेव विरष्ठ प्रबंधक | ASHWANI SACHDEV 100737 SENIOR MANAGER | ASHWANISACHDEV@NTPC.CO.IN | 9650991390 | 12:57:13 | A NEW NLMI "LMI | 059" HAS BEEN PREPARED W.R.T REF OGN DOCUMENT "COSISO00 | 059". | THE DOCUMENT HAS BEEN REVIEWED AND FOUND THAT ALL THE GUIDELINES PERTAINING TO SUBCRITICAL BOILERS HAVE | CA MAY PLEASE ACCORD APPROVAL FOR THIS NEW LMI WITH REF NO. LMI | 18:02:05 | THIS IS NA NEW LMI FOR "BOILER COOLING CUM PRESERVATION" PREPARED W.R.T. OGN DOC "COSISO00 | THE LMI ATTACHED AS ANNEXURE "BOILER COOLING CUM PRESERVATION PROCEDURE " MAY PLEASE BE APPROVED. | 16:00:52 | 15:56:22 | 16:28:42 | NEW LMNI IS REVIEWED W.R.T OGN. | AS PER LMI | WB IS COVERED AS PER USUAL PRACTICE. | 10:02:27 | 11:58:44 | PL REVIENW THE LMI AND FORWARD FOR APPROVAL | 16:30:05 | 16:53:23 | OPERATINON DEPARMENT IS FOLLOWING THE ABOVE SAID PROCEDURE | 16:24:09 | 12:50:34 | 19:28:47 | ISSUE NO.0; REVISION NO. 0; | BOILER COOLING CUM | PRESERVATION PROCEDURE | 1.0 TITLE OF LMI BOILER COOLING CUM PRESERVATION | ISSUE0; REV.0; | 6. REVIEWED BY SIGNATURE: | 7. APPROVED BY: SIGNATURE: | HOP NTPC SIMHADRI | 1.0 INDEX 0 | 3.0 SCOPE 1 | 5.0 SUPERSEDED DOCUMENT 1 | 6.0 SPECIFIC INSTRUCTIONS 1 | 7.0 PROCEDURE | 8.0 ANNEXUREA 6 | EXPENSION INDICATOR | RECORDS | 9.0 ANNEXURE B 7 | ESTINATED MTTR | AND OTHER FORMS OF | BOILER DURING SHUTDOWN PERIODS TO PREVENT CORROSION | DETERIORATION. THIS INCLUDES PROCEDURES FOR GRADUALLY COOLING DOWN THE BOILER TO AVOID | THERMAL STRESS | DRAINING WATER AND REMOVING ANY REMAINING IMPURITIES | AND APPLYING | APPROPRIATE PRESERVATION MEASURES TO SAFEGUARD CRITICAL COMPONENTS. THE GOAL IS TO | MAINTAIN THE INTEGRITY AND LONGEVITY OF THE BOILER SYSTEM | ENSURING IT CAN BE SAFELY RESTARTED | AND OPERATED EFFICIENTLY AFTER THE SHUTDOWN PERIOD. | STAGE 1 | 2 AT NTPC SIMHADRI. | THE SCOPE OF THIS LMI IS SUB CRITICAL DRUM BOILERS STAGE 1 | THE OBJECTIVE OF THIS LMI IS ESTABLISHING THE BOILER COOLING CUM PRESERVATION PROCEDURE TO MINIMIZE | OPTIMIZE COOLING TIME AND IF REQUIRED TO SWITCH FOR | STRESSES IN THE BOILER DURING THE SHUTDOWN PROCESS | BOILER PRESERVATION IN CASE OF RSD | 7.0 PROCEDURE: | SI. NO. ACTIVITIES RESPONSIBILITIES REMARKS | 1 NO FORCE COOLING IS PERMITTED BY DRAINING BOILER HOT | BOILER. | 2 MAXIMUM RATE OF FLUID TEMPERATURE DROP IN DRUM | TYPE BOILER 1.4°C | 3 MAXIMUM DRUM TOP AND BOTTOM DIFFERENCE IN FORCED | 202410:44:20 | 10:44:20 | LMIEMHT1 | 607987 IDATE:22 | VIDE | NEW LMI WAS CREATED VIDE: LMI | 044 TO ADOPT THE OGN ISSUED ABOVE BY CCOS. | LMI COPY IS ATATCHED IN PRADIP NOTE FILE.THE SAME MAY PLEASE BE APPROVED. | PUT UP FOR CONSIDERATION AND APROVAL OF COMPETENT AUTHORITY PLEASE. | जॉनसन प्रसन्ना कुमार कालाडासी विरष्ठ प्रबंधक | 607987 | CHECKEDN AND FORWARDED FOR FURTHER APPROVAL | 16:10:05 | 18:46:42 | 18:55:23 | THE LMNI WAS REVIEWED AND FOUND IN ORDER. | 12:37:33 | 10:07:42 | LMI REVNIEWED AS PER DISCUSSION. | जॉनसन प्रसन्ना कुमार कालाड़ासी विरष्ठ प्रबंधक | 18:17:34 | 19:04:35 | 09:37:36 | 10:57:42 | 11:29:40 | REVIEW. | 21:09:16 | 16:02:48 | 18:14:52 | LMI MONDIFIED AS PER STANDARD FORMAT.PUT UP FOR APPROVAL PLEASE. | 10:21:43 | 11:21:52 | IT IS NEWN LMI REV.0 IS TO BE MENTIONED ON EVERY PAGE ALONG WITH LMI NO. AS PER STANDARD FORMAT | 18:03:03 | NECESSANRY CHANGES AS MENTIONED ABOVE DONE. MAY PLEASE REVIEW AND FROWARD. | जॉनसन प्रसन्ना कुमार कालाड़़ासी विरष्ठ प्रबंधक | 18:31:49 | 09:50:20 | SUBMITTNED FOR REVIEW AND APPROVAL PLEASE. | 17:41:13 | 19:51:43 | 18:37:55 | 09:22:54 | 10:08:25 | NOTE NO:25 O | 12:34:54 | 19:03:18 | 270020 IDATE:26 | CIHMI | 202519:03:18 | SUBJECT:APPROVAL FOR IMPLEMENTATION OF LMI ON ALARM MANAGOEMENT SYSTEM | ALARM OPTIMIZATION IS AN ITERATIVE PROCESS CONSISTING OF: | 1. DATA COLLECTION | DATA ANALYSIS | 2. FIXING PHYSICAL PROBLEMS | 3. IDENTIFYING UNNECESSARY ALARMS AND ELIMINATING THEM | 4. MAKING ENHANCEMENTS TO REQUIRED ALARMS. | 5. CREATING AND OR UPDATING DOCUMENTATION | 6. PERFORMING MANAGEMENT OF CHANGE MOC ALONG WITH PERFORMANCE REVIEW | MOC | 7. IMPLEMENTING | TESTING | AND REPEATING THE ABOVE PROCESS PERIODICAL MANNER | BASED ON OGN REF NO:COSISO00OGN | 005 REV00 ON “GUIDELINES ON ALARM MANAGEMENT | LMI ON ALARM MANAGEMENT SYSTEM HAS BEEN PREPARED FOR NTPC SIMHADRI. | THE OBJECTIVE OF THIS LMI IS TO ENSURE THAT NECESSARY ALARMS ARE ANNUNCIATED WHICH HAVE PREDEFINED | OPERATOR ACTIONS WITH SUITABLE PRIORITIES CONFIGURED IN ALARM SYSTEM FOR OPERATOR TO EFFECTIVELY MANAGE | THE PLANT OR PROCESS UPSETS. | PREPARED LMI AND OGN :COSISO00OGN | 005 HAS BEEN ATTACHED FOR REFERENCE. | PUT UP TO COMPETENT AUTHORITY FOR REVIEW AND APPROVAL FOR IMPLEMENTION OF LMI ON ALARM | MANGEMENT SYSTEM. | 270020 | APPROVNAL MAY KINDLY BE ACCORDED. | ए मोहनदास उप महाप्रबंधक | A MOHANDOSS 020561 DY. GENERAL MANAGER | 9424141781 | AMOHANDOSS@NTPC.CO.IN | 20:40:41 | PUT UP FNOR REVIEW AND APPROVAL FOR IMPLEMENTION OF LMI ON ALARM MANGEMENT SYSTEM. | 21:18:48 | 16:56:37 | 17:52:12 | REQUIREND CHANGES INCOROPRATED AS PER STANDARD FORMAT OF LMI AND REVISED DOCUMENT ATTACHED. | 10:57:25 | 11:59:07 | 11:59:13 | FILE RENVIEWED | 10:28:47 | 15:11:59 | 21:05:38 | 16:40:49 | LMI IS NIN LINE WITH OGN AS IN NOTE #13. | 21:35:40 | 10:33:27 | 10:40:19 | ALARM MANAGEMENT SYSTEM | 005 REV.: 00 | 1 LMI NAME ALARM MANAGEMENT SYSTEM | 005 REV00 | PREPARED BY AJEET KUMAR RAUSHAN | SR.MANAGER C | ANIL KUMAR MAURYA | AGMC | MALAY KANTI JANA | AGMOPRN | SOMNATH BHATTACHARYA | NAVIN KISHORE | REVIEWED BY HEMENDRA KUMAR VERMA | LMI_TPF | 09:47:11 | 299106 IDATE:03 | 202509:47:11 | SUBJECT:LMI FOR HANDLING TOTAL POWER FAILURE IN COAL STATIONO | LMI FOR THE DOC NO. OGNOPOSSTST066 | TITLED "GUIDELINES FOR HANDLING TOTAL POWER FAILURE IN COAL | STATION" DT.21.05.2025 IS PREPARED AND SENT FOR APPROVAL | राजेश कुमार पाढ़ी सहायक प्रबंधक | RAJESH KUMAR PADHY 035245 ASSISTANT MANAGER | RAJESHKUMARPADHY@NTPC.CO.IN | 7978666574 | 299106 | 20:56:54 | 16:24:18 | 11:28:55 | 03:41:43 | REVIEWNED AND FOUND IN LINE WITH OD. | 16:01:12 | सतीश चन्द्र िमश्रा उप महाप्रबंधक | SATISH CHANDRA MISHRA 078593 DY. GENERAL MANAGER | SCMISHRA01@NTPC.CO.IN | 9650872225 | 16:23:17 | 09:04:10 | 11:04:51 | भास्कर वी के कुरीचेट्टी अपर महाप्रबंधक | BHASKAR V K KURICHETY 008045 ADDL. GENERAL MANAGER | 17:02:46 | 10:40:37 | LMI MAY PLEASE BE APPROVED. | 10:48:55 | SUBMITNTED FOR KIND APPROVAL | 09:44:25 | 11:23:51 | 11:50:39 | GUIDELINES FOR HANDLING TOTAL POWER FAILURE IN COAL STATION | REV:00 MAY2025 | 1. 1 LMI NAME GUIDELINES FOR HANDLING TOTAL POWER FAILURE IN COAL | MAY. | 2025 | 4. 4 SUPERSEDED DOCUMENT NOT APPLICABLE | 5. 5 PREPARED BY RAJESH KUMAR PADHY | 6. 6 CHECKED BY SOMNATH BHATTACHARYA | 7. 7 CHECKED BY MALAY KANTI JANA | 8. 8 CHECKED BY NAVIN KISHORE | 9. CHECKED BY NILANJAN MANDAL | 10. 9 CHECKED BY SURESH BABU KOLLA | 11. 1 CHECKED BY ANIL KUMAR MAURYA | 12. 1 CHECKED BY JAYAMOL RACHEL VARUGHESE | 13. CHECKED BY HEMENDRA KUMAR VERMA | REVIEWED AHMAD KAUNAIN RAZA | 14. 1RECHECKED | 2 BY | 15. 1 APPROVED BY SAMEER SHARMA | TITLE GUIDELINES FOR HANDLING TOTAL POWER FAILURE IN COAL STATION | 4. SUPERSEDED DOCUMENTS AND REVISION INDEX 4 | 5. DEFINITION OF BLACK OUT OR TOTAL AC POWER SUPPLY 5 | FAILURE | 6. PREPARATION FOR BLACK OUT 56 | 7. ACTIVITIES TO BE CARRIED OUT IN CASE OF BLACK OUT 79 | 8. RESTORATION 10 | 9. ASSOCIATED DOCUMENT ANNEXURE1 11 | PAGE I 3 | 424772 | 202517:25:31 | 17:25:31 | SUBJECT:LMIMANAGEMENT OF CONDENSER TUBE LEAKAGE IBN SEA | WATER COOLED CONDENSER O | LOCATION MANAGEMENT INSTRUCTION ON MANAGEMENT OF CONDENSER TUBE | LEAKAGE | IN SEA WATER COOLED CONDENSER : | 016 MANAGEMENT OF CONDENSER TUBE LEAKAGE | 1. OFFLINE MONITORING PARAMETERS ARE PRESENTED IN A TABLE. | STEAMWATER SAMPLES ARE ALSO SPECIFIED. | 3. ACTION LEVELS HAVE BEEN REVISED IN ACCORDANCE WITH COSODCHEM001 GUIDELINES. | GUIDELINES. | 5. UPDATED THE ACTIVITIES TO BE CONDUCTED UNDER ACTION LEVELS 1 AND 2. | 6. UPDATED CLAUSE 9.0 RECORDS TO BE MAINTAINED. | BOTH REPORTS ARE TO BE SIGNED BY THE RESPECTIVE S AS SPECIFIED IN THE ABOVE. | LEAKAGE. | 09:58:01 | 18:54:52 | LMI IS NIN LINE WITH THE REVISED OGN. FORWARDED FOR FURTHER REVIEW. | 09:53:26 | PLEASE RNEVIEW THE LMI | 11:36:22 | LMI REVNIEWED AND IS IN LINE WITH THE REVISED OGN. | 11:49:36 | FORWARNDED FOR FURTHER REVIEW AND APPROVAL. | 18:06:34 | PLEASE RNEVIEW THE LMI. | 18:40:25 | FOUUNDT OK. | 20:45:49 | 21:33:47 | 09:47:47 | SUBMITNTED FOR REVIEW AND KIND APPROVAL | 15:23:51 | 16:20:33 | 20:05:59 | MANAGEMENT OF CONDENSER TUBE LEAKAGE | IN SEA WATER COOLED CONDENSER | REV. NO.: 08 | TITLE MANAGEMENT OF CONDENSER TUBE LEAKAGE IN SEA WATER | COOLED CONDENSER | 016 REV:8 | MANAGEMENT OF CONDENSER TUBE | 1 LMI NAME LEAKAGE IN SEA WATER COOLED | CONDENSER. | 016 REV. NO.: 08 | JUNE. 2025 | REV. NO.:4 | 4 REV. NO.: 07 | V. LALITHADEVI DY.MGR CHEM | SANTANU JANA DGM CHEM | SOMNATH BHATTACHARYA AGMOPRN | NILANJAN MANDAL AGMTMD | ANIL KUMAR MAURYA AGM C | AHMAD KAUNAIN RAZA GM | 8 APPROVED BY SAMEER SHARMA–HOP | SL.NO PARTICULARS PAGE NO | 3.0 RECORDS OF REVISION 4 | 4.0 SCOPE 5 | 5.0 GUIDELINES FOR IDENTIFICATION OF CONDENSER 5 | TUBE LEAKAGE CTL FOR OPERATING UNITS | CTL | 6.0 ACTION LEVELS 7 | ADDRESSING CTL OR INGRESS OF CONTAMINANTS IN | THE STEAMWATER CYCLE | DISTURBANCE DUE TO CTL OR INGRESS OF OTHER | CONTAMINANTS | 9.0 RECORDS TO BE MAINTAINED 16 | 10.0 DISTRIBUTION OF LMI 16 | 11.0 REVIEW OF LMI 17 | CHECKLISTI 17 | CHECKLISTII 19 | ANNEXUREI 21 | 747404 | 202316:04:14 | 16:04:14 | SUBJECT:LMITHE CONTROL OF MARINE FOULING BY CONTINUBOUS | CHLORINATION O | 002 " THE CONTROL OF MARINE FOULING BY CONTINUOUS | CHLORINATION" WAS DUE FOR REVIEW. LMI HAS BEEN REVIEWED AND FOUND NO CHANGES. | REVISION: 06 REVISION DATE: 04.01.2021 REVIEW DATE: 09.01.2023 | LMI WORD COPY IS ENCLOSED . | COMPETENT AUTHORITY MAY PL APPROVE THE LMI FOR IMPLEMENTATION. | लवन्या कलत्थुरु उप प्रबंधक रसायन | 16:11:20 | 19:15:03 | 09:27:03 | 07:57:20 | LATEST ONIN FROM CCOS MAY PLEASE BE ATTACHED. | 15:53:06 | 16:30:55 | BY CONTINUOUS CHLORINATION " IS ENCLOSED. | 16:38:53 | 17:09:33 | 18:47:39 | 15:48:02 | 11:32:12 | 16:42:00 | REVIEWNED AND FORWARDED FOR APPROVAL | 18:03:35 | 18:05:41 | 22:34:46 | 00:25:42 | LOCAL MANAGEMENT INSTRUCTIONLMI | REVISION DATE: 04.01.2021 | REVISION: 06 | THE CONTROL OF MARINE FOULING BY | CONTINUOUS CHLORINATION | APPROVED BY: GGM SIMHADRI | GGM- SIMHADRI | DATE: …… | NAME SHRI DESIGNATION SHRI | PREPARED BY LAVANYA K DY. MANAGER | DEEPSHIKHA VERMA DGM CHEM | REVIEWED BY PIYUSH SRIVASTAVA AGM CHEM | T.R.RAJAGOPALAN AGMC | CH. SATYANARAYANA AGMSAFETY | DHURJATI PRASAD PATRA GM O | APPROVED BY SANJAY KUMAR SINHA GGMSIMHADRI | 002 REVISION: 06 | SL NO DESCRIPTION PAGE | 0.0 TABLE OF CONTENTS 1 | 4.0 BRIEF THEORY OF FOULING 2 | 5.0 CHLORINATION TO CONTROL OF MACRO AND MICRO FOULING 3 | 6.0 SPECIFIC OPERATING INSTRUCTIONS TO FOLLOW 6 | 7.0 REFERENCE 8 | 8.0 REVIEW 8 | 9.0 ANNEXURE1: LOG SHEET OF ELECTRO CHLORINATION 9 | 10.0 ANNEXURE2: LOG SHEET OF CW CHLORINATION 10 | 202316:17:09 | 373099 IDATE:07 | 16:17:09 | SUBJECT:NEW LMI ON GUIDELINES FOR SAFETY IN ELECTRICAL SYSTEMOS | 043 | NEW OGN NO. COSOGN | REV. NO: 0 JUNE 2023 HAS BEEN ISSUED ON " GUIDELINES FOR | COPY IS ATTACHED HEREWITH. | SAFETY IN ELECTRICAL SYSTEMS" | 043 IS PREPARED FOR ELECTRICAL SAFETY PERTAINING TO | BASED ON THIS OGN | AN LMI NO. LMI | SIMHADRI. LMI COPY IS ATTACHED HEREWITH. | 373099 | 17:08:21 | PLZ REVINEW | 17:47:43 | READ THNE LMI. | 17:12:49 | 16:40:20 | 11:54:33 | 09:39:10 | 09:49:14 | REVIEWNED AND READ THE SUBJECT LMI | सुयार् प्रकाश राव पसुपुरेड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़्ड़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़़ी विरष्ठ प्रबंधक | 18:26:07 | REVIEWNED THE LMI AS PER OGN. | 10:14:24 | NEW LMNI ON GUIDELINES FOR ELECTRICAL SAFETY SYSTEM REVIEWED | 20:33:49 | 10:03:54 | PLEASE ANDD 2 YEARS REVIEW CLAUSE IN LMI | 16:26:01 | REVIEWN CLUASE INCLUDED AT SL.NO.6 | AND THE DOCUMENT IS UPDATED. | 09:23:12 | 15:47:21 | PL EXAMNINE | 10:26:25 | 08:39:02 | 08:46:16 | 09:59:14 | 10:06:37 | 18:11:17 | 17:52:59 | 18:49:20 | 15:37:25 | LMI PONINT 9.19 | 9.33 TO BE REVIEWED AS PER OGN. | 9.32 | LMI POINT 10.1 TABLE 2 | POINT 4 AND 5 MAY BE REVIEWED. | LMI POINT 10.4.3 | तन्मय िसन्हा विरष्ठ प्रबंधक | TANMOY SINHA 101612 SENIOR MANAGER | 9434737629 | TANMOYSINHA@NTPC.CO.IN | 10:49:09 | FUEL TRANSPORTATION | FUEL TRANSPO | ADM_APRV | 645188 | 202411:11:41 | 11:11:41 | REF NO: | 061 IS PUT UP FOR APPROVAL OF COMPETENT AUTHORITY. | 061 DATED NOV 2024 | ENCLOSURES: 1. NEW LMI LMI | 2. OGN COSISO00OGN | MAY BEN APPROVED FOR IMPLEMENTATION PLEASE. | 11:21:31 | 11:31:05 | 11:06:09 | TO BE MENTIONED ALONGWITH LMI NO. ON EVERY PAGE | IT IS RENV. 0 | 11:55:49 | AND MODIFIED LMI IS HERE BY ATTACHED. | REV.0 MNENTIONED ALONG WITH LMI NO. ON EVERY PAGE | SUBMITTED FOR FURTHER PROCESSING. | 12:24:49 | 12:28:51 | 15:31:32 | 16:15:04 | LMI IS NIN LINE WITH OGN. | 10:15:24 | 11:17:10 | सोमनाथ राउत अपर महाप्रबंधक | SOMANATH ROUT 006476 ADDL. GENERAL MANAGER | 9437138223 | SOMANATHROUT@NTPC.CO.IN | 17:48:56 | 12:07:27 | 20:01:58 | 06:31:16 | GUIDELINES FOR | 061 REV.0 | NOVEMBER2024 | 1 GUIDELINES FOR SIGNALING AND | LMI NAME | 061 DT.OCT2024 | 4 NIL | NEW LMI | NAME: N NARISMHULU | DEPUTY GENERAL MANAGER FT | 6 CHECKED BY NAME: AMULYA KUMAR BEHERA | 7 NAME: A R KOTESWARA RAO | AGM FM | 8 NAME: NAVIN KISHORE | 10 CHECKED BY NAME: TUSHAR KANUNGO | AGM SAFETY | 9 CHECKED BY NAME: SOMANATH ROUT | AGM IT | 11 REVIEWED BY NAME: S PADMAPRIYA GMTS | NAME: P K JENA G M O | 12 REVIEWED BY | 13 APPROVED BY NAME: S K SINHA | SL. NO. PARTICULARS PAGE NO. | 4.0 ESSENTIAL OF SIGNALLING SYSTEM 1 | 6.0 SPECIAL REQUIREMENTS OF SIGNALING IN 25KV AC ELECTRIFIED AREA 1112 | 7.0 SAFETY 13 | 8.0 PERMIT SYSTEM 14 | 9.0 RECORDS 14 | 10.0 REFERENCES 14 | 11.0 REVIEW 14 | 12.0 DISTRIBUTION OF LMI 14 | 13.0 ANNEXURES 1549 | 5.0 | 5.5.2 | 3 POWER SUPPLY 5.6 DGMFT | 4 AT POWER 5.6.3 DGMFT | 5.6.3 | 5 SPECIAL REQUIREMENTS OF SIGNALLING IN 25 KV AC ELECTRIFIED DGMFT | AREA. | NTP C SIMHADRI | COAL REQUIRED FOR THERMAL POWER PLANTS ARE TRANSPORTED THROUGH RAILWAY SYSTEM. PIT | PLANTS HAVE DEDICATED RAILWAY SYSTEM KNOWN AS MGR SYSTEM AND IN RAIL FED PLANTS COAL IS | TRANSPORTED THROUGH INDIAN RAILWAY. | T SYSTEM IS USED TO CONTROL THE MOVEMENT OF RAKES IN | SIGNALLING | T SYSTEM IN RAILWAY HAS EVOLVED WITH TIME AND WITH EVOLUTION IN | RAILWAY SYSTEM. S | T SYSTEM AND AT NTPC SAME SYSTEM IS | TECHNOLOGY. IR HAS ESTABLISHED | STANDARDIZED S | IMPLEMENTED. | AT BROAD LEVEL | T SYSTEM HAS TWO PURPOSES A TO MOVE THE RAKE SAFELY AND B TO UTILIZE | THE ASSET TRACK OPTIMALLY. RAILWAY SYSTEM IS CAPITAL INTENSIVE SYSTEM HENCE BOTH ASPECTS | TRACK | ARE IMPORTANT. | T SYSTEM ARE A FAILED SAFE | B RELIABLE C SIMPLE AND D UNAMBIGUOUS. | DESIGN FEATURE OF S | T SYSTEM NEED TO BE MAINTAINED AT ALL TIMES TO ENSURE SAFE MOVEMENT | THESE ASPECTS OF S | OF COAL RAKES AND SAFETY OF WORKING PERSONALS. | 4.0 ESSENTIAL OF SIGNALLING SYSTEM | 4.1 GENERAL: | GENERAL USE OF SIGNALS: THE RAILWAY SIGNALS MENTIONED HERE SHALL BE USED FOR CONTROLLING | THE MOVEMENT OF TRAINS IN ALL CASES IN WHICH EXCEPTIONS ARE NOT ALLOWED BY APPROVED SPECIAL | INSTRUCTIONS. | SOME OF THE BASIC REQUIREMENT WHICH NEEDS TO BE ENSURED ARE: | FIXED SIGNALS SHALL BE CLEARLY VISIBLE TO THE LOCO PILOTS OF TRAINS APPROACHING THEM AND SHALL | AUTHORIZED BY SPECIAL INSTRUCTIONS. | IN CASE OF FAILURE OF ANY PART OF ITS CONNECTIONS | EVERY FIXED SIGNAL SHALL BE SO CONSTRUCTED THAT | IT SHALL REMAIN AT | OR RETURN TO ITS MOST RESTRICTIVE ASPECT. | SWYDESP | 406410 | D03 | 202510:34:15 | 10:34:15 | 042 REV:0 JAN 2023 IS DUE FOR | PERIODIC REVIEW. | 042 REV:0 HAS BEEN REVIEWD AND SUGGESTED CHANGES ARE | OF OGN REVISION | 042 REV1. | INCOPORATED IN LMI | 042 REV 1 IS PUT UP FOR REVIEW AND APPROVAL PLEASE. | JAI SHIVHARE 035257 ASSISTANT MANAGER | 9907093452 | JAISHIVHARE@NTPC.CO.IN | CHECKEND AND IS BEING FORWARDED FOR REVIEW AND FURTHER PROCESS PLEASE. | 10:46:43 | LMI REVNIEWED. IT IS IN LINE WITH THE OGN. | 15:44:19 | 10:06:50 | LMI IS NREVIEWED | IN LINE WITH OGN. FORWARDED FOR FURTHER APPROVAL. | बी राज शेखर उप महाप्रबंधक | BATANA RAJA SEKHAR 008273 DY. GENERAL MANAGER | 9445869087 | BRSEKHAR@NTPC.CO.IN | 18:19:26 | 19:26:57 | 15:23:06 | 18:55:30 | 19:27:58 | 042 REV:1 | JULY 2025 | 2 LMI NO LMI | 042 | REV:1 | 3 REFERENCE DOCUMENT COSOGN | 4 SUPERSEDED COSOGN | 5 PREPARED BY RAJENDRA SINGH | DGM EM | 6 CHECKED BY MALAY KANTI JANA | AGMEM | 8 REVIEWED BY NAVIN KISHORE | 9 REVIEWED BY SOMNATH BATTACHARYA | 10 REVIEWED BY HEMENDRA KUMAR VERMA | 11 REVIEWED BY AHMAD KAUNAIN RAZA | 12 APPROVED BY SAMEER SHARMA | NTPC SIMHDARI | S.NO DESCRIPTION PAGE. NO | 2A. SCOPE 4 | 2B. REFERENCE DOCUMENTS 4 | 2C. SUSPENDED DOCUMENTS 4 | 3. RECORDS OF REVISION 56 | SCHEDULE | PROCEDURES | 7. SWITCHYARD EQUIPMENTS TESTING 3455 | 8. SWITCHYARD EQUIPMENTS MAJOR 5666 | OVERHAULING | 9. ACCEPTANCE NORMS 6775 | CONDITIONS | LINE CHARGING 7778 | 11. SWITCHYARD BUS | INSTRUCTIONS | 12. BRIEF OF SWITCHYARD RELATED FAULTS WHICH 7982 | MAY LEAD TO UNIT TRIP | 13. SWITCHYARD STANDART OPERATING 83104 | 14. LIST OF MINIMUM MANDATORY SPARES FOR 105107 | 66KV SWYD: | 765 | 400 | 132 | 220 | P ITEMS FOR AIS 108109 | 15. LIST OF T | KEEPING | 17. REVIEW 111 | 18. CHECKLIST: ANNEXUREA: 112140 | GAS INSULATED IN THE POWER PLANTS ARE ONE OF THE IMPORTANT | AIR INSULATED | GAS INSULATED | SWITCHYARD AIR INSULATED | PARTS WORKING AS THE INTERCONNECTION BETWEEN THE GENERATING STATION AND THE GRID. THE | GENERATED POWER FROM THE GENERATING STATION IS TRANSMITTED TO THE GRID THROUGH THE | SWITCHYARD. SWITCHYARD CAN BE CONSIDERED AS THE BACKBONE OF THE POWER PLANT | WHERE AIR ACTS AS A MEDIUM TO INSULATE DIFFERENT COMPONENTS OF THE SWITCHYARD FROM | PLANTS | EACH OTHER. | OVER THE YEARS | FROM TIMETOTIME CCOS HAS ISSUED SEVERAL GUIDELINES FOR SAFE AND | EQUIPMENT. THE GUIDELINES HAVE | IOMS AND TECHNICAL COMPLIANCE | DOCUMENTS LIKE OIN | OD ETC. FOR QUICK AND EASY REFERENCE OF THE GUIDELINES BY | REV1 | PRACTICES AS PER NEWLY RELEASED TC DOCUMENT REF: COS OGN | 041 | DEC2024. | 2A. SCOPE | THIS LMI IS APPLICABLE TO 400KV AIS SWITCHYARD OF NTPC SIMHADRI AND ALL EQUIPMENT OF | EHV SYSTEM. | 2B. REFERENCE DOCUMENTS | 2C. SUSPENDED DOCUMENTS | REV:0 JAN 2023 | CLAUSE OLD PRACTICE NEW PRACTICE REMARKS | SR NO 7 PRACTICES UPDATED REVISED | SR NO 14 PRACTICES UPDATED REVISED | SR NO 18 II PRACTICES UPDATED REVISED | SR NO 21 PRACTICES UPDATED REVISED | SR NO 42 PRACTICES UPDATED REVISED | SR NO 44 PRACTICES UPDATED REVISED | SR NO 45 PRACTICES UPDATED REVISED | SR NO 46 PRACTICES UPDATED REVISED | SR NO 49 PRACTICES UPDATED REVISED | ADDED SAFE MAINT PRACTICES SR NO 51 | 58 ADDITION | 5.1 YEARLY SCHEDULE 5.1.1 TO | 5.1.8 YEARLY | OH SCHEDULE REVISED | 3 YEAR SCHEDULE FOR 5.1.3 | 05 YEARLY | MONTHLY SCHEDULE FOR | 02 DAILY SCHEDULE REVISED | 5.1.5 01 | 3YEAR SCHEDULE FOR 5.1.8 | SO2 CHECKS ADDED IN 5.1.3 ADDITION | PURITY | 5.2 MONTHLY SCHEDULE FOR 5.2 | OH SCHEDULE FOR 5.2 YEARLY | DGA FREQ FOR AREVA CT ADDED AT SR NO 14. ADDITION | MONTHLY SCHEDULE FOR 5.2 | 18 DAILY SCHEDULE REVISED | 5.3 MONTHLY SCHEDULE FOR 5.3 | 01 DAILY SCHEDULE REVISED | OH SCHEDULE FOR 5.3 YEARLY | 5.4 OH SCHEDULE FOR 5.4 YEARLY | 5.5 OH SCHEDULE FOR 5.5 YEARLY | SOS SCHEDULE FOR 5.5 05 YEARLY | 5.6 QUARTERLY SCHEDULE FOR 5.6 | 01 YEARLY REVISED | OH SCHEDULE FOR 5.6 YEARLY | 5.7 OH SCHEDULE FOR 5.6 YEARLY SCHEDULE REVISED | 5.8 OH SCHEDULE FOR 5.6 YEARLY SCHEDULE REVISED | 5.10. 5.10 02 UPDATED REVISED | PAGE ¦ 5
01 High pressure pipe supporting system .pdf | 247903 | LMI/247903 |  | MECH MAINT- BOILER |  |  |  | 1.0, 2.0, 3.0, 4.0, 6.0, 7.0, 9.0 | 1.0 | [7 empty] | 1.0, 4.0, 6.0, 7.0 |  |  |  | 1.0, 6.0, 7.0 |  |  | 1.0, 6.0 | [67 empty] | 1.0 | 1.0 |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 6.0, 7.0 | 1.0, 6.0, 7.0 | 1.0 | 1.0, 6.0, 7.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 6.0, 7.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 10.0, 7.0, 9.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 9.0 | 9.0 | 9.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 10.0 | 11.0 | 11.0 | 11.0 | 1
05. PlantModificationsFinal.pdf | OD | LMI/OD/GEN/006 |  | MTP |  | 5 | [7 empty] | 2.5 | [81 empty] | 2.1 | [109 empty] | 2.2, 2.3 | [29 empty] | 2 | [12 empty] | 2.5 | [106 empty] | 2.5 | [28 empty] | 2.1 | 2.1 | 2.1, 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | 2.4 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
137 LMI for Handling and disposal of Grass.pdf | OD | LMI/OD/OPS/CIV/015 |  | CIVIL MAINT. |  |  |  | 7.1 | [8 empty] | 2.0 | [218 empty] | 3 | [192 empty] | 2.0 |  |  |  | 2.0 | [124 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.3 | 5.2.3 | 5.2.3 | 5.2.3 | 5.2.3 | 5.2.3 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.1 | 7.1 | 7.1 | 7.1
168 LMI on Operation Documentation System with notesheet.pdf | [7 empty] | 4.1.1, 5.7 | 5.7 |  |  |  | 5.7 | 4.1.1, 5.7 |  |  | 1.0, 2.0, 4.1, 4.1.1, 4.1.2, 4.1.3, 5.1, 5.2, 5.7 |  |  |  | 5.7 |  |  | 4.1.1, 5.7 |  |  |  | 5.7 |  |  | 5.7 | [16 empty] | 5.7 | [7 empty] | 5.7 | [6 empty] | 5.7 | [13 empty] | 5.7 | 5.7 | 5.7 | 5.7 | [10 empty] | 5.7 | [89 empty] | 5.7 | [54 empty] | 4 | [7 empty] | 5.7 | 5.7 |  |  |  | 2.0, 4.1.1, 5.7 | [106 empty] | 5.7 | [128 empty] | 5.7 | [61 empty] | 5.7 | [75 empty] | 5.7 | 5.7 | 5.7 | 5.7 | [6 empty] | 5.4 | 5.4.1 | 5.4.4 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 4.1.1, 5.3, 5.7 | 5.7 | 4.1.1, 5.7 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0, 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.1, 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 4.0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1.1, 5.3 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.2, 5.1, 5.2, 5.3 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.3, 5.3 | 4.1.3 | 4.1.3 | 4.1.3 | 4.1.3 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 4.1.4 | 5.0 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3
172 LMI for guidelines and maintenance of radial fans.pdf | OGN | LMI/OGN/OPS/MECH/013/ |  | MECH MAINT- BOILER |  |  | AUG | [228 empty] | 5
173 LMI for capacity testing of DC NI-CD batteries.pdf | OD | LMI/OD/OPS/ELEC/004- |  | ELECT MAINT |  | 1 | JUL | [6 empty] | 6.1 |  |  | 6.1 | [218 empty] | 6 | [696 empty] | 6.1 | 6.1 | [35 empty] | 6.1 | [59 empty] | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
176 INSULATOR PROTECTION IN POLLUTED ATMOSPHER.pdf | OGN | LMI/OGN/OPS/ELEC/009-INSULABTOR |  | ELECT MAINT- OFF SITE |  |  |  | 1.0, 10.0 | [5 empty] | 4.0, 8.0 |  |  | 3.0, 4.0, 8.0 |  |  |  | 6.0 | [184 empty] | 10.0, 5.0, 7.0 | [29 empty] | 7 | [275 empty] | 11.0 | [214 empty] | 4.0, 8.0 | [49 empty] | 4.0 | [156 empty] | 3.0, 4.0, 8.0 | [211 empty] | 3.0, 4.0, 8.0 | [25 empty] | 4.0, 8.0 | 4.0, 8.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 9.0 | 9.0 | 9.0 | 10.0 | 10.0 | 11.0 | 11.0 | 11.0
183 LMI for maintainance and testing of station earthing system.pdf | 437340 | LMI/437340 |  | ELECT MAINT |  | 7 | JUL | [228 empty] | 8
184 Testing of electrical protection system.pdf | 858312 | LMI/858312 |  | ELECT MAINT |  | 3 | DEC | [228 empty] | 9
189 LMI for working in Confined Space.pdf | 504384 | LMI/504384 |  | MECH MAINT- BOILER | [231 empty] | 10
193 Inspection of Boiler tube weld joints by PAUT.pdf | OGN | LMI/OGN/OPS/MECH/047 |  | MECH MAINT- BOILER |  |  |  | 1.0 | 1.0 | [7 empty] | 1.0 |  |  |  | 1.0 | [70 empty] | 7.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | [6 empty] | 1.0 |  | 1.0 | 1.0 |  | 1.0 |  |  | 1.0 |  | 1.0 | 1.0 | [115 empty] | 11 | [490 empty] | 1.0 | [692 empty] | 1.0 | [105 empty] | 1.0 | [46 empty] | 1.0 |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0
195 Desalination plant LMI and general layout.pdf |  |  |  | CHEMISTRY |  | 2 | [229 empty] | 12
196 LMI for Operating of CPU.pdf | OGN | LMI/OGN/OPS/CHEM/20 |  | CHEMISTRY |  | 00 | JAN | [228 empty] | 13 | [1555 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0
198 LMI for performance monitoring of CW system.pdf | 499476 | LMI/499476 | In this LMI Changes are made in monitoring sheet of CW/CT/Condenser performance.ACC condenser | MECH MAINT | [231 empty] | 14
201 Inspection & Maintenance guidelines for chimney..pdf | OGN | LMI/OGN/OPS/CIV/005 |  | CIVIL MAINT. |  | 3 | 25.07.2012 | [228 empty] | 15
207 LMI for prevention of coal pipe choking.pdf | OGN | LMI/OGN/OPS/MECH/045 |  | MECH MAINT- BOILER |  | 03 |  | 13.0, 4.0, 5.0, 7.0, 8.2, 8.4, 9.1, 9.6 | [8 empty] | 13.0, 4.0, 5.0, 7.0, 8.4 |  |  |  | 8.3, 9.2, 9.3, 9.4 | [34 empty] | 8.3 | [57 empty] | 13.0, 7.0, 8.4 |  |  | 13.0, 7.0, 8.4 |  | 1.0 | [39 empty] | 4.0 | 4.0 | 5.0 |  | 6.0 | [72 empty] | 16 | [330 empty] | 6.0 | [159 empty] | 13.0, 5.0, 7.0, 8.4 | [859 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [210 empty] | 8.4 | [185 empty] | 13.0, 7.0, 8.4 |  |  | 4.0, 5.0 | [11 empty] | 13.0, 7.0, 8.4 | 13.0, 7.0, 8.4 |  | 1.0 | 1.0 | 6.0 | 7.0, 8.0, 9.0 | 8.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 13.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.0 | 5.0 | 5.0 | 5.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0, 8.1, 8.2, 8.3 | 7.0 | 8.0 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.3 | 8.3 | 8.3 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.2 | 9.2 | 9.3 | 9.3 | 9.3 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.6 | 9.6
210 LMI for Technical compliance with operation division.pdf | 782573 | LMI/782573 | /OGN/GEN/001 review is done as per schedule. In this LMI no changes has been made. | MECH MAINT |  |  |  | 4.0 | 6.1, 6.2 |  |  |  |  | 2.0 |  |  | 1.0, 3.0, 4.0, 5.0, 5.4, 6.2, 7.0, 8.0 |  |  |  | 3.0, 4.0, 5.3 | [34 empty] | 4.0, 5.4, 6.3, 7.0, 8.0 | [28 empty] | 4.0, 5.4, 7.0, 8.0 | [66 empty] | 3.0 | [53 empty] | 3.0 | [29 empty] | 17 | [12 empty] | 2.0, 4.0, 5.4, 7.0, 8.0 | [308 empty] | 1.0 | [130 empty] | 2.0 | [37 empty] | 2.0, 4.0, 5.4, 7.0, 8.0 | [1444 empty] | 4.0, 5.4, 7.0, 8.0 |  |  |  | 2.0 | [13 empty] | 4.0, 5.4, 7.0, 8.0 |  | 1.0 | 4.0 | 6.0 | 7.0 | 8.0 | 8.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.4 | 5.4 | 5.4 | 6.1 | 6.1 | 6.1 | 6.1 | 6.3 | 6.3 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 1.0 | 1.1 | 1.1.1 | 1.1.1 | 1.1.2 | 1.1.2 | 1.1.3 | 1.1.3 | 1.1.3 | 1.1.4 | 1.1.4 | 1.1.5 | 1.1.6 | 2.0 | 2.1 | 2.2 | 2.2 | 2.3 | 2.4 | 3.0 | 3.1 | 3.2 | 4.0 | 4.1 | 4.2 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 1.0 | 1.1 | 1.1.1 | 1.1.2 | 1.1.3 | 2.0 | 2.1 | 2.2 | 2.2
211 clean conditions during major overhaul of Generators.pdf | OGN | LMI/OGN/OPS/ELEC/020 |  | ELECT MAINT |  |  |  | 1.0 | [5 empty] | 12.0, 4.0 |  |  | 12.0, 3.0, 4.0 |  |  |  | 1.0 | [214 empty] | 18 | [490 empty] | 12.0, 3.0, 4.0 | [206 empty] | 12.0, 3.0, 4.0 | [258 empty] | 2.0 | [12 empty] | 4.0 | [9 empty] | 6.0 | [1132 empty] | 12.0 | 12.0 | 12.0 | 12.0, 4.0 | 4.0 | [18 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 9.0 | 9.0 | 10.0 | 11.0 | 12.0 | 12.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
213 Operation & maintainance practice of APH.pdf | 843466 | LMI/843466 |  | MECH MAINT- BOILER | [231 empty] | 19
215 LMI for Prevention & detection of generator rotor earthe fault.pdf | 566909 | LMI/566909 |  | ELECT MAINT | [231 empty] | 20
229. LMI dissolved gas analysis of transformers and reactors.pdf | OGN | LMI/OGN/OPS/ELEC/19-DISSOLVED |  | ELECT MAINT |  |  |  |  | 11.0, 4.0 |  |  |  |  | 11.0, 2.0, 4.0 |  |  | 11.0, 2.0, 4.0 |  |  |  | 6.01 | [137 empty] | 4.0 | [76 empty] | 21 | [321 empty] | 1.0 | [8 empty] | 3.0 | [124 empty] | 3.0 | [34 empty] | 11.0, 2.0, 4.0 | [206 empty] | 11.0, 2.0, 4.0 | [319 empty] | 11.0, 4.0 | [1095 empty] | 11.0, 2.0, 4.0 | 11.0, 2.0, 4.0 | [28 empty] | 9.0 | [194 empty] | 11.0 | 1.0, 11.0 | [7 empty] | 4.0 | [6 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 6.01 | 6.01 | 6.02 | 6.03 | 6.03 | 6.04 | 6.05 | 6.06 | 6.07 | 7.0 | 9.0 | 10.0 | 11.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 4.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01
233. LMI inspection and maintenance of structures in the vicinity of corrosive chemicals.pdf | 816829 | LMI/816829 |  | CIVIL MAINT. |  |  |  | 14.0, 3.0, 5.0 | [8 empty] | 14.0, 4.0, 5.0 |  |  |  | 1.1, 1.3 | [92 empty] | 14.0, 5.0 |  |  | 14.0, 5.0 | [118 empty] | 22 | [195 empty] | 14.0, 4.0, 5.0 | [294 empty] | 14.0, 4.0, 5.0 | [115 empty] | 1.1 | [743 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | [424 empty] | 2.0 |  |  |  |  | 3.0 | [647 empty] | 14.0, 5.0 |  |  | 14.0, 5.0 | 5.0 | [46 empty] | 14.0, 5.0 |  | 7.0 | 8.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 14.0, 5.0 | 14.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 1.0 | 1.0 | 1.0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1, 4.0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0
234 LMI for Inspection and Maintainance of Machine foundation.pdf | 316965 | LMI/316965 |  | CIVIL MAINT. | [231 empty] | 23
237 LMI for management of DC supply system failure.pdf | OD | LMI/OD/OPS/ELEC/002 |  | ELECT MAINT | [231 empty] | 24
239 LMI inspection and maintenance of storm water drains.pdf | OGN | LMI/OGN/OPS/CIV/006/ |  | CIVIL MAINT. |  |  |  | 2.0 | [8 empty] | 10.0, 3.0, 4.0, 5.0, 6.0, 8.0 |  |  |  | 6.0, 7.0, 8.0 | [95 empty] | 10.0, 5.0, 6.0 | [42 empty] | 3.0 | [12 empty] | 6.0 | [62 empty] | 25 | [120 empty] | 10.0, 4.0, 5.0, 6.0 | [74 empty] | 10.0, 3.0, 4.0, 5.0, 6.0 | [103 empty] | 8.0 | [190 empty] | 10.0, 4.0, 5.0, 6.0 | [465 empty] | 2.0 | [11 empty] | 3.0 | [1385 empty] | 1.0 | [390 empty] | 10.0, 5.0, 6.0 | [9 empty] | 10.0, 5.0, 6.0 | 10.0 | 2.0 | 3.0 | 4.0 | 5.0 | 7.0 | 9.0 | 10.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 8.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 10.0 | 10.0
243. LMI WaterAudits.pdf | OGN | LMI/OGN/OPS/SYST/034 |  | EEMG |  |  | MAR | 1.0 | 7.0 |  |  |  |  | 2.0 |  |  | 1.0, 11.0, 2.0, 6.1 |  |  |  | 4.2, 5.0, 6.4 | [63 empty] | 1.0, 11.0, 6.1 | [150 empty] | 26 | [128 empty] | 1.0, 11.0, 6.1 | [63 empty] | 1.0, 11.0, 2.0, 6.1 | [128 empty] | 1.0 | [130 empty] | 2.0 | [37 empty] | 1.0, 11.0, 2.0, 6.1 | [1467 empty] | 7.0 | [395 empty] | 1.0 | [179 empty] | 4.2, 6.1 | [319 empty] | 1.0, 11.0, 6.1 | [12 empty] | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 9.0 | 10.0 | 11.0 | 1.0, 11.0, 6.1 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.1 | 4.2, 6.1 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0
245 LMI on Chemical control of water steam circuit of boiler water.pdf | OD | LMI/OD/OPS/CHEM/001 |  | CHEMISTRY | [231 empty] | 27
246. CoolingWaterTreatmentOGN_OPS_CHEM19.pdf | OGN | LMI/OGN/OPS/CHEM/019 | MONITORING AND CHEMICAL CLEANING OF CONDENSER TUBES: | CHEMISTRY |  |  | JUL | [228 empty] | 28
248. LMI guidelines for issue of LMI as controlled doc.pdf | OIN | LMI/OIN/GEN/002 |  | EEMG |  | 04 | [7 empty] | 2.0 |  |  | 2.0 | [6 empty] | 2.0 | [31 empty] | 5.2, 6.0, 7.2, 9.0 | [28 empty] | 11.0, 6.0 | [7 empty] | 9.0 | [142 empty] | 29 | [12 empty] | 11.0, 2.0, 6.0 |  |  |  |  | 11.0, 2.0, 6.0 |  |  | 8.0 | [107 empty] | 11.0, 6.0 | [192 empty] | 1.0 | [90 empty] | 8.0 | [39 empty] | 2.0 | [1901 empty] | 1.0 | [566 empty] | 3.0 | [248 empty] | 11.0, 6.0 | [7 empty] | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0 | 9.0 | 10.0 | 11.0 | 11.0, 6.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 9.0 | 9.0 | 9.0 | 9.0 | 10.0 | 11.0 | 11.0
250. LMI on thermal performance of Cooling Towers.pdf | 33587 | LMI/33587 | exception points. | MECH MAINT | [12 empty] | 3.0, 6.0 | [38 empty] | 6.0 | [28 empty] | 6.0 | [150 empty] | 30 | [321 empty] | 1.0 | [7 empty] | 3.0 | [160 empty] | 3.0, 6.0 | [841 empty] | 3.0 | [242 empty] | 3.0, 6.0 | 6.0 | [358 empty] | 6.0 | [50 empty] | 6.0 | [34 empty] | 8.1 | [1250 empty] | 6.0 | 6.0 | [23 empty] | 1.0 | 1.0 | 1.0 | 1.0, 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 8.0 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
251 Performance testing of condenser air extraction plant.pdf | 454565 | LMI/454565 |  | MECH MAINT |  | 02 |  | 1.0 | [5 empty] | 2.0 |  |  | 1.0, 2.0, 5.0, 5.1, 5.2, 6.0 |  |  |  | 5.2.1, 7.0 | [34 empty] | 5.0, 6.0 | [28 empty] | 5.0, 6.0 | [95 empty] | 6.0 | [54 empty] | 31 | [490 empty] | 2.0, 5.0, 6.0 | [1084 empty] | 2.0, 5.0, 6.0 | 5.0, 6.0 | [358 empty] | 5.0, 6.0 | [828 empty] | 1.0 | [614 empty] | 5.0, 6.0 | 5.0, 6.0 | [12 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 5.2.1 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0
252. LMI Determination of Sp water consumption.pdf | OIN | LMI/OIN/OPS/SYST/034 |  | EEMG |  | 03 | APR | 1.0 | [5 empty] | 2.0 |  |  | 1.0, 2.0, 8.0 |  |  |  | 1.0 | [34 empty] | 4.3, 4.4 | [28 empty] | 1.0, 8.0 | [150 empty] | 32 | [17 empty] | 1.0, 2.0, 8.0 | [110 empty] | 1.0, 8.0 | [63 empty] | 1.0, 2.0, 8.0 | [128 empty] | 1.0 | [130 empty] | 2.0 | [1901 empty] | 1.0 | [244 empty] | 1.0 | [254 empty] | 2.0 | [12 empty] | 2.0 | 3.0 | [46 empty] | 1.0 |  |  |  | 1.0 |  | 3.0 | 3.0 | [27 empty] | 4.4 | [571 empty] | 1.0, 8.0 |  |  |  |  | 4.0 | 5.0 | 6.0 | 7.0 | 8.0 | 1.0, 8.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.3, 4.4 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4
260. LMI on system of audit of LMI.pdf | 90042 | LMI/90042 | 05/OGN/GEN/003 REV : 03 MAY 2022 | EEMG |  | 03 | MAY | 1.0, 5.1.2, 5.2.2, 5.3.2 | 5.1.2, 5.2.2 |  |  | 5.1.2 | 3.0, 5.1.2, 5.1.5, 5.2.2, 5.3.1, 5.3.2, 5.4, 7.0 | 3.0, 5.1.2 |  |  | 1.0, 5.1.2, 5.2.2, 5.3.2 |  |  |  | 5.1.2, 5.1.6, 5.5.2 | [6 empty] | 5.1.2 |  |  | 5.1.2 | [16 empty] | 5.1.2 | [5 empty] | 5.1.2 | 5.1.2 | 3.0, 4.0, 5.1.2, 5.1.3, 5.1.4, 5.1.5, 5.2.1, 5.2.2, 5.3.1, 5.3.2, 5.4, 7.0 | 5.1.2 | 5.1.2 | 5.1.2 |  |  |  | 5.1.2 | [5 empty] | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 |  | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 |  |  |  | 5.1.2 | [94 empty] | 5.1.2 | [24 empty] | 5.2.2 | [29 empty] | 33 | [12 empty] | 3.0, 4.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | [7 empty] | 5.1.2 | [98 empty] | 5.1.2 | [128 empty] | 5.1.2 | [12 empty] | 5.1.2 | [7 empty] | 5.1.2 | [40 empty] | 5.1.2 | [92 empty] | 5.1.2 | 5.1.2 | [41 empty] | 1.0 | [43 empty] | 3.0, 5.1.2, 5.1.3, 5.1.5, 5.3.1, 7.0 | [11 empty] | 5.1.2 | [34 empty] | 1.0 |  |  |  | 1.0 |  |  |  | 1.0 |  |  |  |  | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | [11 empty] | 5.0 | [81 empty] | 5.2.2 | [718 empty] | 5.3.2 | [129 empty] | 5.1.2 | [82 empty] | 5.1.2 |  |  |  |  | 5.1.2 | [351 empty] | 5.1.2 |  | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | 5.1.2 | 5.1.2 | [14 empty] | 5.1.2 | [183 empty] | 2.0 | [1117 empty] | 5.1.2 |  |  | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 |  |  |  | 5.1.2 | 5.1.2 | [40 empty] | 4.0 | [302 empty] | 5.1.2 |  |  |  | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | 4.0 |  |  |  | 4.0, 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | 3.0, 5.1.2, 5.1.5, 5.3.1, 7.0 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 3.0, 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 5.1.2 | 1.0 | 3.0 | 4.0 | 5.0 | 5.1 | 5.2 | 5.2 | 5.3 | 5.4 | 5.5 | 5.6 | 5.7 | 5.8 | 5.9 | 5.9 | 5.10 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 5.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.1 | 5.1.3 | 5.1.3 | 5.1.3 | 5.1.3 | 5.1.3 | 5.1.4 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.6 | 5.1.6 | 5.1.6 | 5.1.6 | 5.1.6 | 5.1.6 | 5.1.6 | 5.2 | 5.2.1 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2, 5.3.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.2 | 5.2.3 | 5.2.3 | 5.2.3 | 5.3 | 5.3.1 | 5.3.1 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.3.2 | 5.4 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5.1 | 5.5.1 | 5.5.1 | 5.5.1 | 5.5.2 | 5.5.2 | 5.5.2 | 5.5.2
262 LMI for shaft voltage & current in large turbo generators.pdf | 528517 | LMI/528517 |  | ELECT MAINT | 3 | 3 | APR | [6 empty] | 1.3, 14.0, 6.0 |  |  | 3.0 |  |  |  | 1.2 | [214 empty] | 34 | [173 empty] | 1.3 | [316 empty] | 1.3, 14.0, 4.0, 6.0 | [206 empty] | 1.3, 14.0, 3.0, 4.0, 6.0 | [233 empty] | 10.0 | [24 empty] | 2.0 | [998 empty] | 1.0 | [156 empty] | 1.3, 14.0, 6.0 |  | 4.0 | [32 empty] | 14.0 | [7 empty] | 3.0 |  |  |  | 5.0 | [604 empty] | 1.0 | [1025 empty] | 1.3, 14.0, 4.0, 6.0 | [5 empty] | 4.0 | [18 empty] | 1.3, 14.0, 6.0 | 1.3, 14.0, 6.0 | [10 empty] | 1.1 | 1.2 | 1.3 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0 | 10.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0, 7.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0
263 LMI for inspection of water cooled generator stator winding.pdf | OGN | LMI/OGN/OPS/ELEC/008 |  | ELECT MAINT |  |  |  | 4.0 | [8 empty] | 4.0, 9.0 |  |  |  | 4.0 | [63 empty] | 4.0, 9.0 | [150 empty] | 35 | [128 empty] | 4.0, 9.0 | [12 empty] | 4.0 | [179 empty] | 1.0 | [8 empty] | 2.0, 3.0 | [121 empty] | 2.0 | [37 empty] | 4.0, 9.0 | [115 empty] | 4.0 | [90 empty] | 4.0, 9.0 | [49 empty] | 4.0 | [1606 empty] | 1.0 | [566 empty] | 3.0 | [256 empty] | 2.0 | 3.0 | [387 empty] | 1.0 | [397 empty] | 4.0, 9.0 | [13 empty] | 4.0, 9.0 | 4.0, 9.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.0 | 6.0 | 7.0 | 7.0 | 8.0 | 9.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0
268. POLICY ON TECHNICAL MANAGEMENT SYSTEM.pdf | 105535 | LMI/105535 |  | EEMG | 01 | 02 | MAY 2022 |  | 6.0 |  |  |  | 4.0, 5.2, 5.3, 6.0 | 3.0 |  |  | 1.0, 2.0, 4.0, 5.1, 5.2, 6.0 |  |  |  | 5.1 | [34 empty] | 4.0, 5.2, 5.3, 6.0 | [179 empty] | 36 | [12 empty] | 3.0, 4.0, 5.2, 6.0 | [316 empty] | 3.0 | [1546 empty] | 1.0 | [58 empty] | 4.0, 5.2, 6.0 |  |  |  | 3.0 | [414 empty] | 1.0 | [402 empty] | 2.0 | [548 empty] | 4.0 | [97 empty] | 5.1 | [228 empty] | 4.0, 5.2, 6.0 | [66 empty] | 2.0 | [367 empty] | 4.0, 5.2, 6.0 | 4.0, 5.2, 6.0 | 4.0, 5.2, 6.0 | [10 empty] | 6.0 | 3.0 | 4.0 | 5.0 | 5.1 | 5.2 | 5.3 | 6.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 6.0
274 Examination of turbine lub oil.pdf | OGN | LMI/OGN/OPS/CHEM/009 |  | CHEMISTRY |  |  |  | 1.0, 4.5 | [5 empty] | 2.0, 4.3, 4.8, 9.0 |  |  | 0.0007, 2.0, 4.3, 4.5, 4.6, 4.8, 9.0 |  |  |  | 0.0007, 5.0 | [130 empty] | 3.0 | [28 empty] | 4.1, 4.6 | [54 empty] | 37 | [153 empty] | 4.5 | [167 empty] | 1.0 | [168 empty] | 2.0, 4.3, 4.8, 9.0 | [115 empty] | 0.0007, 2.0, 4.1, 4.2, 4.4, 4.5 | [948 empty] | 1.0 | 2.0 | 3.0 | [1859 empty] | 2.0 | [43 empty] | 1.0 | [734 empty] | 4.3, 4.8, 9.0 | 4.3, 4.8, 9.0 |  |  | 4.0 | 6.0 | 7.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 9.0 | 9.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.2 | 4.2 | 0.0007 | 0.0007 | 0.0007 | 0.0007 | 0.0007 | 4.3 | 4.3, 4.7, 4.8 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
277 LMI for Unloading of bulk chemicals.pdf | OGN | LMI/OGN/OPS/CHEM/007 |  | CHEMISTRY | 08 |  |  | 8.0 | 8.0 |  |  |  | 8.0 |  |  |  | 8.0 |  |  |  | 8.0 | [6 empty] | 8.0 |  |  | 8.0 | [8 empty] | 8.0 | [7 empty] | 8.0 |  |  |  | 8.0 |  |  |  | 8.0 | [6 empty] | 8.0 | [172 empty] | 38 | [12 empty] | 8.0 | [20 empty] | 8.0 |  | 8.0 |  | 8.0 | 8.0 | 8.0 |  |  |  | 8.0 | [8 empty] | 8.0 | 8.0 |  |  |  |  | 8.0 | [9 empty] | 8.0 | [6 empty] | 8.0 | [6 empty] | 8.0 | [8 empty] | 8.0 |  |  |  | 8.0 | [7 empty] | 8.0 | [9 empty] | 8.0 |  |  | 8.0 | [112 empty] | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 |  | 8.0 | 8.0 | 8.0 | 8.0 | [6 empty] | 8.0 | [22 empty] | 8.0 | [135 empty] | 8.0 | [84 empty] | 8.0 | [115 empty] | 8.0 | [7 empty] | 8.0 | [51 empty] | 8.0 | [6 empty] | 8.0 | [9 empty] | 8.0 |  | 8.0 | [214 empty] | 8.0 |  |  | 8.0 | [180 empty] | 8.0 |  | 8.0 | [39 empty] | 8.0 | [11 empty] | 8.0 | [28 empty] | 8.0 | [157 empty] | 8.0 | 8.0 | 8.0 | [166 empty] | 8.0 | 8.0 | 8.0 |  |  |  | 8.0 | 8.0 | 8.0 | 8.0 | [27 empty] | 8.0 | [74 empty] | 8.0 | [56 empty] | 8.0 | 8.0 | [30 empty] | 8.0 | [603 empty] | 8.0 | [326 empty] | 8.0 | 8.0 | [70 empty] | 8.0 | 8.0 | 8.0 | 8.0 | [317 empty] | 8.0 | 8.0 | 8.0 | [74 empty] | 8.0 | [1196 empty] | 8.0 | 8.0 |  | 8.0 | [44 empty] | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0
279. CHEMICAL CONTROL OF GENERATOR STATOR PRIMARY WATER SYSTEM.pdf | OGN | LMI/OGN/OPS/CHEM/002 |  | CHEMISTRY |  | 8 |  |  | 10.5, 6.0 |  |  |  | 10.5, 6.0 |  |  |  | 10.5, 6.0 |  |  |  | 10.5, 6.0 | [6 empty] | 10.5, 6.0 | [11 empty] | 10.5, 6.0 | [7 empty] | 10.5, 6.0 | [7 empty] | 6.0 |  |  | 6.0 | [8 empty] | 10.5 | [15 empty] | 6.0 | [96 empty] | 6.0 | [54 empty] | 39 | [33 empty] | 6.0 |  | 10.5 |  | 10.5 | 10.5 | 10.5 |  |  |  | 6.0 | [8 empty] | 6.0 | 10.5, 6.0 |  |  | 6.0 |  | 6.0 |  |  | 6.0 | 6.0 | 6.0 | 6.0 |  |  |  | 6.0 | [6 empty] | 6.0 | [6 empty] | 6.0 | [8 empty] | 6.0 |  |  |  | 6.0 | [7 empty] | 6.0 | [9 empty] | 10.5 |  |  | 10.5 | [90 empty] | 10.5, 6.0 | [28 empty] | 6.0 | 6.0 | 6.0 | 6.0 |  |  | 10.5, 6.0 | [5 empty] | 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | [8 empty] | 6.0 | [125 empty] | 10.5, 6.0 | [17 empty] | 6.0 | [185 empty] | 6.0 | [14 empty] | 10.5, 6.0 | [7 empty] | 10.5, 6.0 | [20 empty] | 10.5 | 10.5 | 10.5 | 10.5 | [27 empty] | 10.5 | [6 empty] | 10.5 | [9 empty] | 10.5 |  | 10.5 | [24 empty] | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | [370 empty] | 10.5 |  | 10.5 | [36 empty] | 6.0 | [14 empty] | 10.5 | [35 empty] | 10.5 | [18 empty] | 10.5, 6.0 | [480 empty] | 6.0 | [20 empty] | 10.5, 6.0 | [1002 empty] | 6.0 | 6.0 | 6.0 | 6.0 |  |  |  | 6.0 | [313 empty] | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | [1363 empty] | 10.5, 6.0 | 6.0 | [10 empty] | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | 10.5, 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
281. Residual life and condition assessment of RCC and steel structures.pdf | OPS | LMI/OPS/CIVIL/013 |  | CIVIL MAINT. |  | 03 | [7 empty] | 4.0, 5.0 |  |  | 1.0, 3.0, 4.0, 5.0 |  |  |  | 5.0 | [138 empty] | 3.0 | [45 empty] | 2.0 | [29 empty] | 40 | [195 empty] | 4.0, 5.0 | [96 empty] | 5.0 | 5.0 | [5 empty] | 3.0 | [21 empty] | 1.0 | [168 empty] | 5.0 | [1808 empty] | 5.0 | [209 empty] | 2.0 | [1190 empty] | 2.0 | [350 empty] | 5.0 | [226 empty] | 2.0 | [151 empty] | 5.0 | [113 empty] | 5.0 | [30 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0
283. Long-term preservation of materials.pdf | 01 | LMI/01/C |  | STORES | 01 |  | MAR | [228 empty] | 41
289. Guidelines for Ash Dyke Management.pdf | OGN | LMI/OGN/OPS/SYST/022 |  | ASH DYKE MANAGEMENT |  |  | MAR | [228 empty] | 42
292 LMI for security policies for control system.pdf | OGN | LMI/OGN/OPS/C |  | C & I MAINT |  | 04 | [10 empty] | 1.0, 2.0, 8.13, 8.7 |  |  |  | 3.0 | [63 empty] | 8.13 | [150 empty] | 43 | [128 empty] | 8.13 | [192 empty] | 1.0 | [130 empty] | 2.0 | [37 empty] | 2.0, 8.13 | [205 empty] | 1.0, 2.0 | [3100 empty] | 1.0 | [1058 empty] | 8.13 | [29 empty] | 8.13 | [5 empty] | 2.0 | [15 empty] | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 4.6 | 4.7 | 4.8 | 4.9 | 4.10 | 4.11 | 4.12 | 4.13 | 4.14 | 4.15 | 4.16 | 4.17 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.8 | 8.9 | 8.10 | 8.11 | 8.12 | 8.12 | 8.12 | 8.12 | 8.13 | 8.13 | 8.13 | 8.13 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 4.0 | 4.1 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0 | 4.1.0
296. BOILER TUBE FAILURE analysis and control.pdf | OGN | LMI/OGN/OPS/MECH/049 |  | MECH MAINT- BOILER |  |  |  | 15.0 | [8 empty] | 15.0 |  |  |  | 15.0 | [92 empty] | 15.0 |  |  | 15.0 | [55 empty] | 7.0 | [62 empty] | 44 | [490 empty] | 15.0 | [115 empty] | 15.0 | [324 empty] | 15.0 | [418 empty] | 1.0 | [1765 empty] | 15.0 | [1875 empty] | 15.0 | [26 empty] | 2.0 | 3.0 | 4.0 | 5.0 | 5.0 | 6.0 | 6.0 | 7.0 | 8.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0 | 15.0
300 LMI for Nagative Phase sequence alarm at generating stations.pdf | OGN | LMI/OGN/OPS/ELEC/023 |  | ELECT MAINT | [231 empty] | 45
301. GENERATOR ROTOR END WINDING RETAINING RINGS.pdf | OGN | LMI/OGN/ELEC/005 |  |  | 1 | 5 | OCT 2023 | 1.0, 8.0 | 10.0 |  |  |  | 6.0 | 11.0, 12.0, 4.0, 7.0 |  |  | 1.0, 11.0, 3.0, 4.0, 5.0, 6.0, 8.0 |  |  |  | 6.0 | [214 empty] | 46 | [490 empty] | 11.0, 12.0, 4.0, 7.0 | [115 empty] | 5.0, 8.0, 9.0 | [43 empty] | 6.0 | [46 empty] | 11.0, 12.0, 3.0, 4.0, 7.0 | [258 empty] | 2.0 | [12 empty] | 4.0 | [9 empty] | 6.0 | [377 empty] | 9.0 | 10.0 | [280 empty] | 11.0, 12.0, 4.0, 7.0 | [472 empty] | 11.0, 12.0, 4.0, 7.0 | [22 empty] | 1.0 | 2.0 | 3.0 | 4.0 | [8 empty] | 12.0 | 1.0 | [148 empty] | 11.0, 12.0, 4.0, 7.0 | [1535 empty] | 5.0 | [44 empty] | 4.0 | [29 empty] | 7.0 | [436 empty] | 6.0 | [901 empty] | 11.0, 12.0, 4.0, 7.0 | [5 empty] | 6.0 | 7.0 | 11.0 | 12.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 3.0 | 3.0, 4.0 | 3.0 | 3.0, 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 8.0, 9.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 9.0 | 9.0 | 9.0 | 10.0 | 10.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 11.0 | 12.0 | 12.0 | 12.0 | 12.0
302. ELECTRICAL TESTING OF GENERATOR ROTOR WINDING INSULATION.pdf | OGN | LMI/OGN/OPS/ELEC/004 |  | ELECT MAINT | [9 empty] | 1.0, 12.0 |  |  | 1.0, 12.0, 3.0 |  |  |  | 2.0 | [214 empty] | 47 | [330 empty] | 4.0 | [159 empty] | 1.0, 12.0 | [205 empty] | 1.0, 12.0 | 1.0, 12.0, 3.0 | [212 empty] | 1.0, 12.0 | [45 empty] | 2.0 | [12 empty] | 4.0 | [1165 empty] | 1.0 | [7 empty] | 9.0 |  |  |  | 12.0 | 1.0 | [148 empty] | 1.0, 12.0 | [1532 empty] | 2.0 | 3.0 |  | 5.0 | [44 empty] | 1.0 | [575 empty] | 1.0 | [798 empty] | 6.0 | [99 empty] | 1.0, 12.0 | [15 empty] | 4.0 | 7.0 | 9.0 | 9.0 | 10.0 | 11.0 | 12.0 | 12.0 | 12.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0
304. Handling of electrostatic sensitive devices and handling requirements.pdf | 195567 | LMI/195567 |  | C & I MAINT |  |  | 02.06.2022 | 4.0 | [227 empty] | 48 | [321 empty] | 1.0 | [133 empty] | 3.0 | [3244 empty] | 2.0 | [1823 empty] | 5.0 | 6.0 | 7.0 | 7.0 | 7.0 | 8.0 | 9.0 | 10.0 | 11.0 | 11.0 | 11.0
305. Control of PFA Agglomerate.pdf | BMD | LMI/BMD/664351 |  | MECH MAINT |  | 8.0 |  | 1.0, 4.0, 5.0, 6.0, 7.0, 8.0 | 1.0, 6.0, 7.0, 8.0 | [7 empty] | 0.5, 1.0, 4.0, 5.0, 6.0, 7.0, 8.0 |  |  |  | 7.0 | [34 empty] | 7.0 | [40 empty] | 1.0 | 1.0 | 1.0 |  |  | 1.0 | [6 empty] | 1.0 | [7 empty] | 1.0, 6.0, 7.0, 8.0 | [19 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  |  |  | 6.0 | [72 empty] | 49 | [200 empty] | 8.0 | [100 empty] | 1.0 | 1.0 | [187 empty] | 1.0, 5.0, 6.0, 7.0, 8.0 | [1727 empty] | 1.0 | 1.0 | [9 empty] | 1.0 | 1.0 |  |  | 1.0 | 1.0 |  | 1.0 | 1.0 |  |  | 1.0 | [234 empty] | 1.0 | [138 empty] | 1.0, 5.0, 6.0, 7.0, 8.0 | [1023 empty] | 5.0 | [1926 empty] | 0.5 |  | 1.0, 8.0 | 8.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 6.0, 7.0, 8.0 | 1.0, 7.0 | 1.0, 7.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3.0 | 3.0 | 4.0 | 5.0 | 5.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0, 8.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0 | 8.0
308. PREVENTION OF DAMAGE TO GENERATORS DUE TO MOISTURE IN HYDROGEN.pdf | OGN | LMI/OGN/OPS/SYST/009 |  | CHEMISTRY |  |  | 12.07.2022 | [6 empty] | 2.0, 5.1, 7.0 |  |  | 2.0, 5.1, 7.0 |  |  |  | 3.0 | [184 empty] | 5.1, 5.2, 5.3, 5.4, 5.5, 5.6 | [29 empty] | 50 | [192 empty] | 2.0, 5.1, 7.0 | [297 empty] | 2.0, 5.1, 7.0 | [115 empty] | 5.6 | [302 empty] | 5.1, 7.0 | [442 empty] | 3.0 | [432 empty] | 3.0 | [978 empty] | 1.0 | [102 empty] | 2.0 | [549 empty] | 2.0 | [2341 empty] | 5.2 | [6 empty] | 5.1, 7.0 | 5.1, 7.0 | 5.1, 7.0 |  |  |  | 0.0 | 1.0 | 4.0 | 4.0 | 5.0 | 5.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 2.0 | 2.0 | 3.0 | 4.0 | 4.0 | 4.0 | 5.0 | 5.0 | 5.1 | 5.1, 5.2, 5.3, 5.4, 5.5, 5.6 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
315. GUIDELINES FOR ORT MEETING.pdf | 326144 | LMI/326144 |  | EEMG |  |  | JUL | 2.0, 6.2.7 | 6.2.7 |  |  | 6.2.7 | 1.0, 2.0, 3.0, 6.1.1, 6.1.4, 6.1.5, 6.2.1, 6.2.7, 7.0 | 2.0, 3.0, 6.1.1, 6.1.4, 6.2.7, 7.0 |  |  | 1.0, 2.0, 3.0, 4.0, 6.1.1, 6.1.4, 6.1.6, 6.2.3, 6.2.7, 7.0 |  |  |  | 6.1.4 | [6 empty] | 6.2.7 |  |  | 6.2.7 | [16 empty] | 6.2.7 | [6 empty] | 6.2.7 | 2.0, 3.0, 6.1.1, 6.1.4, 6.1.5, 6.2.1, 6.2.7, 7.0 | 6.2.7 | 6.2.7 |  |  |  |  | 6.2.7 | [6 empty] | 6.2.7 |  | 6.2.7 | 6.2.7 | 6.2.7 |  |  |  | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 |  |  |  | 6.2.7 | [119 empty] | 6.1.1, 6.1.4 | [29 empty] | 51 | [8 empty] | 6.2.7 | [110 empty] | 2.0, 6.1.1, 6.1.4, 6.2.3, 6.2.7, 7.0 | [5 empty] | 6.2.7 | 6.2.7 | [65 empty] | 2.0, 3.0, 6.1.1, 6.1.4, 6.2.7, 7.0 | [117 empty] | 6.2.7 | [10 empty] | 1.0 | [7 empty] | 3.0 |  | 4.0 | [72 empty] | 6.2.7 | [7 empty] | 6.2.7 | [77 empty] | 2.0, 3.0, 6.1.1, 6.1.4, 6.2.7, 7.0 | [46 empty] | 2.0 |  |  |  | 2.0 |  |  |  | 2.0 |  |  |  |  | 2.0 | [99 empty] | 6.1.4 | [139 empty] | 2.0 | [65 empty] | 2.0 | [74 empty] | 6.2.7 | [76 empty] | 6.2.7 | [87 empty] | 6.2.7 | [26 empty] | 6.2.7 |  |  | 6.2.7 | [479 empty] | 6.2.7 | [147 empty] | 3.0 | [599 empty] | 1.0 | [244 empty] | 2.0 | [658 empty] | 6.2.7 | 6.2.7 | 6.2.7 |  |  |  | 6.2.7 | 6.2.7 | [390 empty] | 2.0 | [404 empty] | 6.2.7 | [368 empty] | 6.1.1 | [772 empty] | 6.1.1 | [654 empty] | 6.2.7 | 6.2.7 |  | 6.2.7 | 1.0, 2.0, 6.1.1, 6.1.4, 6.2.7, 7.0 |  |  | 5.0 | 5.0 | 5.0 | 5.0, 6.2.7 | 5.0 | 5.0 | 5.0 | 5.0 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 2.0, 6.1.1, 6.1.4, 6.2.7, 7.0 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 6.1 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 7.0 | 7.0 | 7.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.0 | 6.2.7 | 6.2.7 | 6.2.7 | 6.2.7 | 6.0 | 6.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.1 | 6.1.2 | 6.1.2 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.3 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.4 | 6.1.5 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.6 | 6.1.7 | 6.1.7 | 6.1.7 | 6.1.7 | 6.1.7 | 6.1.7 | 6.1.7 | 6.1.7 | 6.2 | 6.2.1 | 6.2.1 | 6.2.1, 6.2.2 | 6.2.1 | 6.2.2 | 6.2.2 | 6.2.2 | 6.2.2 | 6.2.2 | 6.2.2 | 6.2.3 | 6.2.3
317. Guide lines for Carrying out Safe Operation of Sky Climbers inside Boiler.pdf | 641558 | LMI/641558 |  | MECH MAINT- BOILER |  |  |  | 1.0, 15.0, 3.0, 4.0, 5.0, 6.0 | 1.0 |  |  |  |  | 5.0 |  |  | 1.0, 15.0, 2.0, 4.0, 5.0, 6.0 |  |  |  | 1.0 | [71 empty] | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | [6 empty] | 1.0 |  | 1.0 | 1.0 |  | 1.0, 15.0 |  |  | 1.0, 15.0 |  | 1.0 | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 |  | 6.0 | [72 empty] | 52 | [17 empty] | 1.0, 5.0 | [472 empty] | 1.0, 15.0 | [159 empty] | 1.0 | [561 empty] | 1.0 | [127 empty] | 1.0 |  |  | 1.0 |  | 1.0 | 1.0 |  |  |  | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [416 empty] | 6.0 | [4312 empty] | 1.0, 5.0 |  |  |  | 1.0, 15.0 | [26 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 7.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 14.0 | 15.0 | 15.0 | 15.0 | 15.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 4.0 | 4.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0
319. Guide lines for Carrying out Safe Erection of Scaffolding inside Boiler.pdf | 984095 | LMI/984095 |  | MECH MAINT- BOILER |  |  |  | 1.0, 17.0, 2.0, 3.0, 4.0, 5.0, 6.0 | 1.0 | [7 empty] | 1.0, 17.0, 4.0, 5.0 |  |  |  | 1.0, 2.0, 3.0 | [34 empty] | 1.0 | [36 empty] | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | [6 empty] | 1.0 |  | 1.0 | 1.0 |  | 1.0, 17.0 |  |  | 1.0, 17.0 |  | 1.0 | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 |  | 6.0 | [72 empty] | 53 | [441 empty] | 17.0 | [48 empty] | 1.0, 17.0 | [530 empty] | 1.0 | [321 empty] | 1.0 |  | 1.0 | 1.0 |  |  |  | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [399 empty] | 1.0, 5.0 | 1.0 | [15 empty] | 6.0 | [4345 empty] | 5.0 | 1.0 |  | 1.0 | 1.0 |  |  |  | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 14.0 | [16 empty] | 4.0 |  |  | 6.0 | [13 empty] | 1.0, 17.0, 5.0 | [27 empty] | 1.0 | 1.0 | 1.0 | 1.0, 17.0 | 1.0, 17.0 | 1.0 | 7.0 | 15.0 | 15.0 | 16.0 | 16.0 | 16.0 | 17.0 | 17.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0
321 LMI for Maintainance and testing of generator excitation control system.pdf | OGN | LMI/OGN/OPS/ELEC/010 |  | ELECT MAINT |  | 00 | OCT | 1.0, 4.1, 4.2, 4.3, 4.4, 9.0 | [5 empty] | 2.0 |  |  | 1.0, 2.0, 4.2, 4.3, 4.4, 9.0 |  |  |  | 5.0 | [63 empty] | 4.2, 4.3, 4.4, 9.0 | [6 empty] | 4.1 | [143 empty] | 54 | [128 empty] | 4.2, 4.3, 4.4, 9.0 | [192 empty] | 1.0 | [8 empty] | 3.0 | [121 empty] | 2.0 | [37 empty] | 2.0, 4.2, 4.3, 4.4, 9.0 | [27 empty] | 4.1 | [178 empty] | 2.0, 4.2, 4.3, 4.4, 9.0 | [1257 empty] | 1.0 | [30 empty] | 4.2 | [34 empty] | 4.3 | [9 empty] | 4.4 | [45 empty] | 8.0 | [739 empty] | 7.0 | [103 empty] | 3.0 | [374 empty] | 9.0 | [688 empty] | 5.0 | 6.0 |  | 7.0 | [2165 empty] | 4.4 | [91 empty] | 4.2, 4.3, 4.4, 9.0 | 4.2, 4.3, 4.4, 9.0 |  | 2.0 |  |  |  |  | 2.0 | 3.0 | 4.1 | 4.2 | 4.3 | 4.4 | 5.0 | 7.0 | 8.0 | 9.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 4.1 | 4.1 | 4.1 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3, 4.4 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 5.0 | 5.0 | 6.0 | 7.0 | 8.0 | 8.0
326. Attemperator spray nozzles and liners.pdf | 366215 | LMI/366215 |  | MECH MAINT- BOILER |  |  |  | 1.0, 2.0, 4.0, 6.0, 9.0 | 1.0 | [7 empty] | 1.0, 4.0, 6.0, 9.0 | 7.0, 9.0 |  |  | 1.0 |  |  | 1.0, 6.0, 9.0 | [67 empty] | 1.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 |  |  |  | 1.0 |  |  | 1.0 |  |  |  | 1.0 | 1.0, 6.0, 9.0 |  |  | 1.0, 6.0, 9.0 |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 |  |  |  | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 | 4.0 | 5.0 |  | 6.0 | [9 empty] | 7.0 | [35 empty] | 7.0 | [8 empty] | 7.0 | 9.0 |  |  |  |  | 9.0 | [11 empty] | 55 | [306 empty] | 1.0 | 1.0 | [182 empty] | 1.0, 6.0, 9.0 | [159 empty] | 6.0 | [1824 empty] | 1.0 | [3096 empty] | 1.0 | [14 empty] | 1.0 | [58 empty] | 9.0 | [782 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 6.0, 9.0 | 1.0, 6.0, 9.0 | 1.0 | 1.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 | 9.0
328. Boiler access and viewing doors.pdf | 370414 | LMI/370414 |  | MECH MAINT- BOILER |  |  |  | 1.0, 14.0, 2.0, 4.0, 6.0, 7.0, 9.0 | 1.0 | [7 empty] | 1.0, 14.0, 4.0, 6.0 |  |  |  | 1.0 | [70 empty] | 7.0 |  |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 |  | 1.0 |  | 1.0 |  |  | 1.0 |  |  |  |  | 1.0, 14.0, 6.0 |  |  | 1.0, 14.0, 6.0 |  |  | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 |  | 6.0 | [9 empty] | 7.0 | [32 empty] | 7.0 |  |  | 7.0 | 7.0 | [7 empty] | 7.0 | 9.0 | [11 empty] | 7.0 |  |  |  |  | 56 | [305 empty] | 1.0 |  |  |  |  | 1.0 | [109 empty] | 1.0 | [69 empty] | 1.0, 14.0, 6.0 | [859 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [410 empty] | 1.0 | [5 empty] | 6.0 | [167 empty] | 5.0 | [4495 empty] | 1.0 | 1.0 | [51 empty] | 7.0 | [14 empty] | 5.0 | [21 empty] | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 14.0, 6.0 | 1.0, 14.0, 6.0 | 1.0 | 7.0 | 8.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 14.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 4.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 9.0
329. Power station drainage.pdf | OPS | LMI/OPS/CIVIL/002-POWER |  | CIVIL MAINT. | [231 empty] | 57
333. THERMOGRAPHIC SURVEY OF BOILER FURNACE WALL & SCW TUBES.pdf | 387427 | LMI/387427 |  | MECH MAINT- BOILER |  |  | 1.0 | 7.0 | 1.0 | [7 empty] | 1.0, 14.0, 4.0, 6.0, 7.0 | 9.0 |  |  | 1.0, 7.0 | [70 empty] | 7.0 |  |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 |  | 1.0 |  | 1.0 |  |  | 1.0 |  |  |  |  | 1.0, 14.0, 6.0 | [5 empty] | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 |  | 6.0 | [9 empty] | 7.0 | [35 empty] | 7.0 | 7.0 | [7 empty] | 7.0 | 9.0 | [16 empty] | 58 | [192 empty] | 1.0, 14.0, 4.0, 6.0 | [112 empty] | 1.0 |  |  |  |  | 1.0 | [109 empty] | 1.0 | [69 empty] | 1.0 | [849 empty] | 1.0 | [9 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [410 empty] | 1.0 | [5 empty] | 6.0 | [404 empty] | 1.0 | [4258 empty] | 1.0 | 1.0 | [51 empty] | 7.0 | [44 empty] | 1.0 |  | 1.0 | 1.0 | 1.0 |  |  |  | 7.0 | 8.0 | 10.0 | 11.0 | 12.0 | 13.0 | [12 empty] | 4.0 |  |  | 6.0 | [6 empty] | 7.0 | [77 empty] | 2.0 | [32 empty] | 1.0, 9.0 |  | 1.0 | 1.0, 14.0, 6.0 | 1.0 | 1.0 | 1.0, 14.0, 6.0 | 1.0, 14.0, 6.0 | 1.0 | 14.0 | 14.0, 6.0 | 14.0, 6.0 | 14.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 9.0
336. Operation and maintenance of sewage treatment plant.pdf | OGN | LMI/OGN/ENV/011 |  | CHEMISTRY |  |  | MAR | [228 empty] | 59
337. Guidelines for coal mill maintenance.pdf | OGN | LMI/OGN/OPS/MECH/052/ | REVISION NO. 1.00, DATE: JAN'2023”.As per LMI, 2-yearly review was due in December'22. | MECH MAINT- BOILER | 1 | 1.00 | [229 empty] | 60
338. Sampling and analysis of coal.pdf | 746909 | LMI/746909 |  | CHEMISTRY |  | 4 |  | 3.2, 4.2.1 | [8 empty] | 1.0, 3.1, 4.1.2, 4.2, 4.2.1, 5.5 |  |  |  | 1.0, 4.1.2, 5.2 | [214 empty] | 61 | [321 empty] | 1.0 | [284 empty] | 3.2, 4.1.2, 4.2 | [389 empty] | 5.5 | [2820 empty] | 1.0 | [3039 empty] | 3.1, 4.1.2, 4.2, 5.5 | [20 empty] | 1.0, 3.1, 4.1.2, 4.2, 5.5 | 1.0, 3.1, 4.1.2, 4.2, 5.5 | 3.1, 4.1.2, 4.2, 5.5 | [6 empty] | 3.1 | 4.1 | 4.1 | 4.2 | 4.2 | 4.3 | 4.4 | 4.4 | 4.5 | 4.6 | 4.7 | 4.7 | 4.8 | 4.8 | 4.9 | 4.9 | 5.0 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.5 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.2 | 3.2 | 3.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.0, 4.1 | 4.0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.1 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.1.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1 | 4.2.1
339. Operation and maintenance guidelines for variable pitch axial fans.pdf | BMD | LMI/BMD/674289 |  | MECH MAINT | [231 empty] | 62
340. The startup Shutdown layup procedures of Water Steam circuits of Plant.pdf | 300846 | LMI/300846 |  | CHEMISTRY | [231 empty] | 63
343 LMI for high current bus bar system connected to generator and generator transformer.pdf | OGN | LMI/OGN/OPS/ELEC/035 |  | ELECT MAINT | [231 empty] | 64
348. BOILER HEADER LIGAMENT CRACKING;GUIDANCE ON INSPECTION POLICY.pdf | 602862 | LMI/602862 |  | MECH MAINT- BOILER |  |  |  | 1.0, 14.0, 2.0, 4.0, 6.0, 7.0, 9.0 | 1.0 | [7 empty] | 1.0, 14.0, 2.0, 4.0, 6.0, 7.0 |  |  |  | 1.0, 7.0 | [70 empty] | 7.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | 1.0 | 1.0 |  | 1.0 |  |  | 1.0 |  | 1.0 | 1.0 |  | 1.0, 14.0, 6.0, 7.0 |  |  | 1.0, 14.0, 6.0, 7.0 |  | 1.0 | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 | 4.0 | 5.0 |  | 6.0 | [9 empty] | 7.0 | [35 empty] | 7.0 | [9 empty] | 9.0 |  |  |  | 9.0 | 9.0 | [11 empty] | 65 | [490 empty] | 1.0, 14.0, 6.0, 7.0 | [166 empty] | 7.0 | [38 empty] | 1.0, 14.0, 6.0, 7.0 | [653 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [416 empty] | 6.0 | [737 empty] | 7.0 | [3062 empty] | 1.0 |  |  |  | 1.0 | [10 empty] | 14.0 | [58 empty] | 7.0 | [790 empty] | 1.0 |  |  | 1.0 | [18 empty] | 3.0 | [8 empty] | 6.0 | [21 empty] | 9.0 |  | 9.0 | 9.0 |  | 9.0 | 9.0 | [44 empty] | 7.0 | 8.0 | 10.0 | 11.0 | 12.0 | 13.0 | [697 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 14.0, 6.0, 7.0 | 1.0, 6.0 | 14.0 | 14.0, 7.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 9.0
349.. Boiler thermal expansion indicator and use.pdf | 623630 | LMI/623630 |  | MECH MAINT- BOILER |  |  |  | 1.0, 15.0, 4.0, 5.0, 8.0 | 1.0 | [7 empty] | 1.0, 15.0, 4.0, 5.0 |  |  |  | 1.0, 5.0 | [70 empty] | 7.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 |  | 1.0 |  | 1.0 |  |  | 1.0 |  |  |  |  | 1.0, 15.0, 5.0 |  |  | 1.0, 15.0, 5.0 |  | 1.0 | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 | [11 empty] | 5.0 | [32 empty] | 10.0 | [11 empty] | 8.0 | 9.0 |  |  | 10.0 | 10.0 | 10.0 | [8 empty] | 11.0 |  |  | 66 | [120 empty] | 1.0, 15.0, 5.0 | [173 empty] | 1.0 | [10 empty] | 1.0 | [184 empty] | 1.0, 15.0, 5.0 | [849 empty] | 1.0 | [9 empty] | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | [3667 empty] | 5.0 | [261 empty] | 2.0 | [290 empty] | 1.0 |  |  |  |  | 1.0 |  | 1.0 | [84 empty] | 8.0 | [819 empty] | 8.0 |  |  |  |  | 10.0 | [48 empty] | 8.0 | 10.0 | 11.0 | [12 empty] | 3.0 |  | 4.0 | [18 empty] | 9.0 | [766 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 15.0, 5.0 | 1.0, 15.0, 5.0 | 1.0 | 7.0 | 12.0 | 13.0 | 14.0 | 15.0 | 15.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 5.0 | 8.0 | 8.0 | 8.0 | 9.0 | 10.0 | 10.0 | 11.0
35 Inspection and maintenance of steel and concrete structures (non-corrosive atmosphere).pdf | OGN | LMI/OGN/OPS/CIV/007 |  | CIVIL MAINT. |  | 8 | MAY | [228 empty] | 67
350. Maintenance of integrity of boiler support susyem.pdf | 611938 | LMI/611938 |  | MECH MAINT- BOILER |  |  |  | 1.0, 14.0, 3.0, 4.0, 5.0, 7.0, 8.0, 9.0 | 1.0 | [7 empty] | 1.0, 14.0, 4.0, 5.0, 7.0 |  |  |  | 1.0, 7.0 | [70 empty] | 7.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | 1.0 | 1.0 |  | 1.0 |  |  | 1.0 |  | 1.0 | 1.0 |  | 1.0, 14.0, 5.0, 7.0 |  |  | 1.0, 14.0, 5.0, 7.0 | 1.0 | 1.0 | 1.0 | [15 empty] | 14.0 | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 | 4.0 | 5.0 |  | 6.0 | [8 empty] | 5.0 | 7.0 | [32 empty] | 7.0, 8.0 |  |  |  | 8.0 | [8 empty] | 9.0 | [16 empty] | 68 | [371 empty] | 7.0 | [118 empty] | 1.0, 14.0, 5.0, 7.0 | [849 empty] | 1.0 | [5 empty] | 1.0 |  |  |  | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | [4312 empty] | 8.0 | [872 empty] | 7.0 | 8.0 | [706 empty] | 1.0 | 1.0 | 1.0 |  | 1.0 | [103 empty] | 13.0 | 14.0 | [125 empty] | 1.0, 14.0, 5.0, 7.0 | [18 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 14.0, 7.0 | 10.0 | 11.0 | 12.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 8.0 | 8.0 | 8.0 | 8.0
351. Boiler hydraulic leak testing during breakdown repairs.pdf | 608694 | LMI/608694 |  | MECH MAINT- BOILER |  |  |  | 1.0, 14.0, 4.0 | 1.0 | [7 empty] | 1.0, 14.0, 2.0, 4.0 |  |  |  | 1.0, 2.0 | [70 empty] | 7.0 | 1.0 |  |  |  | 1.0 | 1.0 | 1.0 |  |  | 1.0 | 1.0 | 1.0 |  | 1.0 |  |  | 1.0 |  | 1.0 | 1.0 |  | 1.0, 14.0 |  |  | 1.0, 14.0 | 1.0 | 1.0 | 1.0 | [15 empty] | 14.0 | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 | [74 empty] | 69 | [294 empty] | 1.0 | [195 empty] | 1.0, 14.0 | [854 empty] | 1.0 |  |  |  |  | 1.0 | 2.0 | 3.0 | 4.0 | 5.0 | [284 empty] | 1.0, 14.0 | [114 empty] | 1.0 | 1.0 | [15 empty] | 6.0 | [4763 empty] | 1.0 | [5 empty] | 7.0 | 8.0 | [806 empty] | 1.0 | [7 empty] | 13.0 | 14.0 | [150 empty] | 10.0 | 11.0 | 12.0 | [131 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 14.0 | 1.0, 14.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 3.0 | 4.0 | 5.0 | 5.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0 | 6.0
352. Performance optimization of PT plant, chlorination system CLO2.pdf |  |  |  | CHEMISTRY | [231 empty] | 70
354 Code of practices on power plant chemistry.pdf | OGN | LMI/OGN/OPS/CHEM/015 |  | CHEMISTRY | 04 | 00 | [229 empty] | 71
357. LMI reliability improvent matrix.pdf | OGN | LMI/OGN/OPS/SYST/057 |  | FUEL HAND.- OPN |  | 0 | JAN | 1.5, 2.0 | [5 empty] | 1.0, 3.2, 4.0 |  |  | 1.0, 2.0, 3.2, 4.0 |  |  |  | 1.0 | [115 empty] | 2.0 | [98 empty] | 72 | [192 empty] | 1.0, 3.2, 4.0 | [297 empty] | 1.0, 3.2, 4.0 | [2718 empty] | 4.0 | [33 empty] | 3.2 | [1427 empty] | 1.0 | [273 empty] | 1.0 | [793 empty] | 1.2 | [2107 empty] | 3.2, 4.0 | [9 empty] | 1.1 | 1.2 | 1.3 | 2.0 | 3.0 | 3.1 | 3.2 | 4.0 | 1.0, 3.2, 4.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.2 | 3.2 | 3.2 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0
361 LMI for Duct & expansion joint maintainance.pdf | DUCT | LMI/DUCT/847230 |  | MECH MAINT- BOILER |  |  |  | 5.0, 6.0, 6.1, 6.2 | [12 empty] | 1.0 | [214 empty] | 73 | [2356 empty] | 3.0 | [5650 empty] | 2.0 | 4.0 | 6.2 | 6.3 | 7.0
362 LMI for Safe work practices in electrified track section.pdf | OGN | LMI/OGN/OPS/SYST/058 |  | MGR |  |  |  | 1.0, 4.0, 6.0, 7.0, 9.4, 9.5, 9.7 | [8 empty] | 2.1, 23.94, 9.7 |  |  |  | 23.94, 9.6, 9.7 | [63 empty] | 23.94 | [120 empty] | 9.7 | [29 empty] | 74 | [150 empty] | 9.1 | [41 empty] | 2.1, 23.94, 9.7 | [64 empty] | 4.0 | [232 empty] | 2.1 | [494 empty] | 23.94 | [768 empty] | 23.94, 9.7 | [1009 empty] | 1.0 | [644 empty] | 23.94 | [1745 empty] | 1.0 | [485 empty] | 1.0 | [883 empty] | 23.94, 9.7 | [1486 empty] | 9.7 | [27 empty] | 23.94, 9.7 | 23.94, 9.7 | [41 empty] | 1.0 | 2.0 | 2.1 | 3.0 | 5.0 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.5 | 7.0 | 8.0 | 9.0 | 9.1 | 9.2 | 9.2 | 9.3 | 9.5 | 9.6 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0, 23.94 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 23.94 | 2.0 | 2.1 | 2.1 | 2.1 | 3.0 | 4.0 | 4.0
363 LMI for Boiler cooling & preservation procedure.pdf |  |  |  | MECH MAINT- BOILER |  |  | 1.0 | 1.0, 2.0 | [8 empty] | 1.0, 4.0, 7.0 |  |  |  | 1.0 | [63 empty] | 1.0 | [11 empty] | 1.0 | 1.0 | 1.0 |  |  | 1.0 |  | 1.0 |  |  |  |  | 1.0 | [10 empty] | 1.0 | [16 empty] | 2.0 | [14 empty] | 3.0 | [6 empty] | 4.0 |  | 5.0 |  | 6.0 | [72 empty] | 75 | [153 empty] | 1.0 | [38 empty] | 1.0, 4.0 | [55 empty] | 1.0 | [61 empty] | 1.0 | [179 empty] | 1.0 | [849 empty] | 1.0 |  |  | 1.0 | [421 empty] | 1.0 | [591 empty] | 4.0 | [249 empty] | 2.0 | [3925 empty] | 1.0 |  |  | 1.0 | 1.0 | [21 empty] | 4.0 | [152 empty] | 5.0 | [1269 empty] | 1.0 | [24 empty] | 2.0 | [269 empty] | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 3.0 | 5.0 | 6.0 | 7.0 | 8.0 | 8.0 | 8.0 | 9.0 | 9.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 3.0 | 3.0 | 3.0 | 6.0 | 6.0 | 6.0 | 6.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0 | 7.0
364.LMI for Guidlines on HT switchgear maintenance practices.pdf | OGN | LMI/OGN/OPS/ELEC/044 |  | ELECT MAINT | [231 empty] | 76
365. LMI on Alarm management system.pdf |  |  |  | C & I MAINT |  | 00 | [229 empty] | 77
366.LMI on Guideline for handling of total power failure in coal station.pdf |  |  |  | OPERATION |  |  | 21.05.2025 | [228 empty] | 78
80 Management of Condenser Tube Leakages in Sea water cooled condenser.pdf | OGN | LMI/OGN/OPS/CHEM/016 | LEAKAGE | CHEMISTRY | [16 empty] | 7.0 | [214 empty] | 79 | [606 empty] | 8.0 | [1348 empty] | 1.0 | [4298 empty] | 2.0 | [2293 empty] | 3.0 | 4.0 | 5.0 | 5.0 | 5.0 | 6.0 | 7.0 | 7.0 | 8.0 | 8.0 | 9.0 | 10.0 | 11.0 | 11.0 | 11.0 | 11.0
99 The control of Marine fouling by Continuous Chlorination.pdf | OIN | LMI/OIN/OPS/CHEM/002 |  | CHEMISTRY |  | 06 | 04.01.2021 | [228 empty] | 80 | [1352 empty] | 3.0 | [1514 empty] | 2.0 | [2905 empty] | 1.0 | [2838 empty] | 0.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0 | 9.0 | 10.0
Guidelines for safety in electrical system.pdf | OGN | LMI/OGN/OPS/ELEC/043 |  | ELECT MAINT- MAIN PLANT |  |  | JUN | [228 empty] | 81
Guidelines for Signalling and Telecommunication system.pdf | OGN | LMI/OGN/OPS/SYST/061 |  | FUEL TRANSPORTATION |  |  | NOV | 13.0, 5.0 | [8 empty] | 13.0 |  |  |  | 1.0, 13.0, 4.1 | [214 empty] | 82 | [128 empty] | 13.0 | [63 empty] | 13.0 | [128 empty] | 1.0 | [130 empty] | 2.0 | [34 empty] | 13.0 |  |  | 13.0 | [1863 empty] | 1.0 | [566 empty] | 3.0 | [256 empty] | 2.0 | 3.0 | [29 empty] | 4.1 | [3502 empty] | 2.0, 3.0 | [2002 empty] | 13.0 | [21 empty] | 4.0 | 6.0 | 7.0 | 8.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 13.0 | 13.0 | 13.0 | 13.0 | 13.0 | 13.0 | 13.0 | 13.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 4.0 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
LMI_Guidelines on AIS Stations Maintenance Practices (2).pdf | OGN | LMI/OGN/OPS/ELEC/042 |  | ELECT MAINT |  | 1 | JAN | [228 empty] | 83 | [455 empty] | 3.0 | [8435 empty] | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 5.1 | 5.1.8 | 5.1.5, 5.1.8, 5.2, 5.3, 5.4, 5.5, 5.6 | 5.1.8 | 5.1.5, 5.1.8 | 5.1.8 | 5.1.5, 5.2 | 5.1.5 | 5.1.5 | 5.1.5 | 5.1.5 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 5.3 | 5.4 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 5.10 | 5.10